## Sheet1
Count of INCIDENCE | Column Labels
Row Labels | 2022 | 2023 | 2024 | 2025 | Grand Total
HARDY EX LANGATA | 23 | 36 | 34 | 28 | 121
3rd PARTY/FOREIGN INTERFERENCE | 1 |  |  |  | 1
CONDUCTORS | 2 | 5 | 2 | 2 | 11
CONTROLLED INTERRUPTION | 7 | 6 | 14 | 6 | 33
EQUIPMENT FAILURE | 1 |  | 1 |  | 2
LOSS OF SUPPLY | 6 | 19 | 14 | 18 | 57
OTHERS (Non-Breakdown Related) |  | 1 |  |  | 1
POLE |  | 1 |  | 1 | 2
TRANSFORMER |  |  |  | 1 | 1
TREE/ OBJECT CONTACT | 6 | 4 | 3 |  | 13
ICOLO EX LANGATA |  |  |  | 2 | 2
LOSS OF SUPPLY |  |  |  | 2 | 2
KAREN HOSPITAL EX LANGATA | 15 | 12 | 30 | 10 | 67
CONDUCTORS | 2 |  | 3 | 1 | 6
CONTROLLED INTERRUPTION | 3 | 1 | 6 | 2 | 12
IRREGULAR SUPPLY |  |  | 1 |  | 1
LOSS OF SUPPLY | 9 | 9 | 17 | 5 | 40
TREE/ OBJECT CONTACT | 1 | 2 | 3 | 2 | 8
KUWINDA EX LANGATA | 28 | 31 | 24 | 17 | 100
CONDUCTORS | 1 | 2 |  |  | 3
CONTROLLED INTERRUPTION | 9 | 4 | 7 | 3 | 23
EQUIPMENT FAILURE | 1 |  |  |  | 1
FUSE | 1 |  |  |  | 1
IRREGULAR SUPPLY |  | 1 |  |  | 1
LOSS OF SUPPLY | 16 | 23 | 14 | 11 | 64
TREE/ OBJECT CONTACT |  | 1 | 2 | 3 | 6
VANDALISM |  |  | 1 |  | 1
MAGADI EX LANGATA | 35 | 35 | 53 | 31 | 154
3rd PARTY/FOREIGN INTERFERENCE |  |  | 1 |  | 1
CONDUCTORS | 6 | 3 | 1 | 3 | 13
CONTROLLED INTERRUPTION | 7 | 9 | 11 | 12 | 39
EQUIPMENT FAILURE | 2 | 1 | 1 |  | 4
FUSE |  |  | 1 |  | 1
LOSS OF SUPPLY | 18 | 20 | 35 | 15 | 88
POLE |  | 2 |  |  | 2
TRANSFORMER |  |  | 1 |  | 1
TREE/ OBJECT CONTACT | 1 |  | 2 | 1 | 4
VANDALISM | 1 |  |  |  | 1
NDALATI EX LANGATA | 24 | 34 | 28 | 12 | 98
3rd PARTY/FOREIGN INTERFERENCE |  |  |  | 2 | 2
CONDUCTORS | 1 | 1 | 1 |  | 3
CONTROLLED INTERRUPTION | 2 | 9 | 10 | 4 | 25
LOSS OF SUPPLY | 19 | 20 | 13 | 6 | 58
POLE |  | 1 |  |  | 1
TRANSFORMER |  |  | 1 |  | 1
TREE/ OBJECT CONTACT | 2 | 3 | 3 |  | 8
NGEI EX LANGATA | 23 | 33 | 18 | 26 | 100
3rd PARTY/FOREIGN INTERFERENCE |  | 1 |  |  | 1
CABLE |  | 2 | 3 |  | 5
CONDUCTORS | 1 | 2 | 1 |  | 4
CONTROLLED INTERRUPTION | 4 | 8 | 5 | 9 | 26
EQUIPMENT FAILURE |  | 1 |  |  | 1
FUSE | 1 |  |  |  | 1
IRREGULAR SUPPLY |  |  | 1 |  | 1
LOSS OF SUPPLY | 17 | 14 | 6 | 15 | 52
OTHERS (Non-Breakdown Related) |  | 1 |  |  | 1
POLE |  |  |  | 2 | 2
TRANSFORMER |  | 1 | 1 |  | 2
TREE/ OBJECT CONTACT |  | 3 | 1 |  | 4
OTIENDE EX LANGATA | 1 |  | 3 | 4 | 8
CONDUCTORS |  |  |  | 1 | 1
CONTROLLED INTERRUPTION | 1 |  | 1 | 2 | 4
LOSS OF SUPPLY |  |  | 2 |  | 2
TREE/ OBJECT CONTACT |  |  |  | 1 | 1
SOWETO EX LANGATA | 63 | 67 | 98 | 75 | 303
3rd PARTY/FOREIGN INTERFERENCE | 1 |  |  | 1 | 2
CABLE |  |  |  | 2 | 2
CONDUCTORS | 3 | 4 | 1 | 1 | 9
CONTROLLED INTERRUPTION | 16 | 26 | 52 | 41 | 135
EQUIPMENT FAILURE | 1 | 1 | 1 |  | 3
IRREGULAR SUPPLY |  | 1 |  |  | 1
LOSS OF SUPPLY | 39 | 32 | 42 | 28 | 141
OTHERS (Non-Breakdown Related) | 1 |  | 1 | 1 | 3
POLE |  |  | 1 |  | 1
TRANSFORMER |  | 1 |  |  | 1
TREE/ OBJECT CONTACT | 2 | 2 |  | 1 | 5
Grand Total | 212 | 248 | 288 | 205 | 953

## Sheet 1
INCIDENCE | DESC_INCIDENCIA | DETECTION_DATE | FY | RESOLUTION_DATE | CAUSE_SUBTYPE | CAUSE_TYPE | CAUSE | CURRENT_STATUS | REGION | COUNTY | INCIDENCE_TYPE | SR_DURATION | MAX_DEMAND | AFFECTED_CUSTOMERS | INSTALATION | INSTALATION_1 | PARENT | INSTALATION_TYPE | FBBU_NAME | MONTH_YEAR | DURATION_HRS | LOSS_GWHRS | LOSS_MILLION_KSH | NUMERATOR_SAIFI | NUMERATOR_SAIDI
3129602 | To replace shattered fuse mounts | 2024-11-19 17:50 | 2024 | 2024-11-19 18:20 | Hv Fuse | FUSE | BURNT HV FUSE HOLDER | Resolved | Nairobi | Nairobi West County | Non Programmed | 30 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.5 | 0.0014058 | 0.019682 | 5760 | 2880
2944121 | Replace blown fuses - s/s 2212 | 2022-08-04 15:59 | 2022 | 2022-08-04 16:09 | Hv Fuse | FUSE | BLOWN HV FUSE | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.16667 | 0.00047743 | 0.0066841 | 11799 | 1966.5
2987985 | To replace blown spur fuses | 2023-02-25 17:09 | 2022 | 2023-02-25 17:17 | Spur Fuses | FUSE | BLOWN SPUR FUSE | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.13333 | 0.00012841 | 0.0017978 | 1922 | 256.2667
3192705 | controlled | 2025-08-31 18:09 | 2025 | 2025-08-31 21:44 | Mv Pole | POLE | FALLEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 215 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 3.5833 | 0.0072258 | 0.10116 | 3000 | 10750
3045061 | Feeder off on sustained fault | 2023-11-08 22:40 | 2023 | 2023-11-09 12:29 | Mv Pole | POLE | LEANING MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 829 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 13.8167 | 0.020812 | 0.29137 | 2807 | 38783.3833
3062762 | Replace broken poles | 2024-01-27 12:47 | 2023 | 2024-01-27 16:27 | Mv Pole | POLE | BROKEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 220 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 3.6667 | 0.01031 | 0.14433 | 5343 | 19591
3062159 | To recover and relocate poles | 2024-01-24 12:46 | 2023 | 2024-01-24 13:11 | Mv Pole | POLE | FALLEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 25 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.41667 | 0.0011715 | 0.016402 | 5343 | 2226.25
3210402 | Sustained fault | 2025-11-14 15:13 | 2025 | 2025-11-14 19:27 | Mv Pole | POLE | FALLEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 254 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 4.2333 | 0.0123 | 0.17221 | 12796 | 54169.7333
3258440 | Fallen ABS Y2099 | 2026-03-07 18:45 | 2025 | 2026-03-07 20:51 | Mv Pole | POLE | FALLEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 123 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 2.05 | 0.0059565 | 0.083391 | 12796 | 26231.8
3051988 | Knocked pole beyond Y5396 | 2023-12-04 23:06 | 2023 | 2023-12-05 13:57 | Mv Pole | POLE | BROKEN MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 891 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 14.85 | 0.02903 | 0.40642 | 796 | 11820.6
3134451 | Repair burnt short leg structure pole at s/s 33510 | 2024-12-09 12:34 | 2024 | 2024-12-09 19:36 | Mv Pole | POLE | BURNT MV POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 422 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 7.0333 | 0.026234 | 0.36727 | 32702 | 230004.0667
3300143 | Sustained fault beyond ARY5230 | 2026-03-31 18:57 | 2025 | 2026-03-31 21:31 | Secondary Distribution Transformer | TRANSFORMER | INTERNAL DEFECTS AFTER TESTING | Resolved | Nairobi | Nairobi West County | Non Programmed | 154 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 2.5667 | 0.0051757 | 0.07246 | 3056 | 7843.7333
3167655 | CB-AY 5230 | 2025-04-27 11:42 | 2024 | 2025-04-27 17:40 | Secondary Distribution Transformer | TRANSFORMER | INTERNAL DEFECTS AFTER TESTING | Resolved | Nairobi | Nairobi West County | Non Programmed | 358 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 5.9667 | 0.016776 | 0.23487 | 5774 | 34451.5333
3135705 | Ngei ex Langata byd 2099 sustained, Ragati office informed. | 2024-12-15 08:20 | 2024 | 2024-12-16 02:36 | Secondary Distribution Transformer | TRANSFORMER | INTERNAL DEFECTS AFTER TESTING | Resolved | Nairobi | Nairobi West County | Non Programmed | 1096 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 18.2667 | 0.052327 | 0.73257 | 12297 | 224625.2
3049164 | Sustained fault | 2023-11-23 16:51 | 2023 | 2023-11-23 18:24 | Secondary Distribution Transformer | TRANSFORMER | FAULTY TRANSFORMER | Resolved | Nairobi | Nairobi West County | Non Programmed | 93 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 1.55 | 0.0044401 | 0.062162 | 12066 | 18702.3
3147254 | sustained fault | 2025-02-06 20:31 | 2024 | 2025-02-06 20:47 | Secondary Distribution Transformer | TRANSFORMER | INTERNAL DEFECTS AFTER TESTING | Resolved | Nairobi | Nairobi West County | Non Programmed | 16 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.26667 | 0.00052131 | 0.0072983 | 925 | 246.6667
3049451 | Sustained fault beyond AY5302 | 2023-11-24 16:45 | 2023 | 2023-11-24 19:46 | Secondary Distribution Transformer | TRANSFORMER | FAULTY TRANSFORMER | Resolved | Nairobi | Nairobi West County | Non Programmed | 181 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 3.0167 | 0.011252 | 0.15753 | 33331 | 100548.5167
3003531 | Sustained fault on Hardy ex Langata. | 2023-04-25 18:44 | 2022 | 2023-04-25 19:52 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 68 | 1506.3 | 2649 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 1.1333 | 0.0017071 | 0.0239 | 2649 | 3002.2
2969246 | Tree branch on the line byd AY146 | 2022-11-26 09:57 | 2022 | 2022-11-26 15:09 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 312 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 5.2 | 0.0078328 | 0.10966 | 2561 | 13317.2
3078306 | Sustained fault | 2024-04-01 01:51 | 2023 | 2024-04-01 14:28 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 700 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 11.6667 | 0.017573 | 0.24603 | 2832 | 33040
2962271 | Feeder off on syustained fault | 2022-10-29 03:12 | 2022 | 2022-10-29 10:57 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 465 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 7.75 | 0.011674 | 0.16343 | 2561 | 19847.75
2940803 | Tree branch on the line | 2022-07-20 14:55 | 2022 | 2022-07-20 16:40 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 105 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 1.75 | 0.002636 | 0.036904 | 2406 | 4210.5
3117620 | A trip on Hardy ex Langata.Nyameya informed. | 2024-09-27 19:23 | 2024 | 2024-09-27 21:20 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE FELL ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 117 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 1.95 | 0.0029373 | 0.041122 | 2958 | 5768.1
3070475 | Sustained fault | 2024-02-28 19:46 | 2023 | 2024-02-28 22:29 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 163 | 1506.3 | 2827 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 2.7167 | 0.0040921 | 0.05729 | 2827 | 7680.0167
3166054 | Sustained fault on Hardy ex Langata between AY 5137 and AY 1118. Wamalwa informe | 2025-04-21 12:08 | 2024 | 2025-04-21 14:43 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 155 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 2.5833 | 0.0038913 | 0.054478 | 2964 | 7657
3095079 | Suatained btwn AY1104 & AY 113 | 2024-06-03 22:12 | 2023 | 2024-06-04 11:39 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 807 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 13.45 | 0.02026 | 0.28364 | 2832 | 38090.4
3029716 | Conductors on a leanig pole shorting with trees | 2023-09-06 10:24 | 2023 | 2023-09-06 12:32 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 128 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 2.1333 | 0.0032134 | 0.044988 | 2654 | 5661.8667
3173157 | KUWINDA EX LANGATA | 2025-05-21 16:21 | 2024 | 2025-05-21 17:07 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 46 | 963 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.76667 | 0.0007383 | 0.010336 | 2155 | 1652.1667
3063361 | Sustained fault Kuwinda ex Langata Karen office informed. | 2024-01-30 12:04 | 2023 | 2024-01-30 18:13 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 369 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 6.15 | 0.0059231 | 0.082923 | 1991 | 12244.65
3289329 | Sustained fault | 2026-03-24 08:57 | 2025 | 2026-03-24 13:46 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE FELL ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 289 | 963.1 | 1819 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 4.8167 | 0.0046389 | 0.064945 | 1819 | 8761.5167
3205103 | To cut tree a branch encroaching 66Kv line | 2025-10-25 14:41 | 2025 | 2025-10-25 15:12 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 31 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.51667 | 0.0004976 | 0.0069664 | 1796 | 927.9333
3200673 | Sustained fault on Kuwinda ex Langata, Siriba informed. | 2025-10-06 09:45 | 2025 | 2025-10-06 11:05 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 80 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 1.3333 | 0.0012841 | 0.017978 | 1796 | 2394.6667
3157066 | Sustained fault | 2025-03-18 11:41 | 2024 | 2025-03-18 12:52 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 71 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.1833 | 0.0011397 | 0.015955 | 2155 | 2550.0833
3060100 | Sustained fault on Karen Hospital ex Langata beyond AY 122. Karen office emergen | 2024-01-15 01:52 | 2023 | 2024-01-15 08:39 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 407 | 692.9 | 1081 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 6.7833 | 0.0047002 | 0.065802 | 1081 | 7332.7833
3166689 | Sustained fault on Karen hospital ex Langata .Informed Nyamwea. | 2025-04-23 16:08 | 2024 | 2025-04-23 16:50 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 42 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.7 | 0.00048503 | 0.0067904 | 1206 | 844.2
3347658 | Karen Hospital ex Langata sustained, Siriba informed. | 2026-04-16 16:03 | 2025 | 2026-04-16 17:09 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 66 | 0 | 1133 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 1.1 | 0 | 0 | 1133 | 1246.3
3073244 | Sustained fault | 2024-03-11 16:27 | 2023 | 2024-03-11 18:12 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 105 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 1.75 | 0.0012126 | 0.016976 | 1092 | 1911
3130816 | Karen Hospital Ex Langata Sustained, Kipchumba informed | 2024-11-25 02:05 | 2024 | 2024-11-25 10:52 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 527 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 8.7833 | 0.006086 | 0.085204 | 1188 | 10434.6
3236326 | Sustained fault on Karen Hospital ex Langata. Karen Office informed. | 2026-02-01 14:12 | 2025 | 2026-02-01 17:45 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 213 | 0 | 1097 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 3.55 | 0 | 0 | 1097 | 3894.35
3159168 | Tree branch on power line | 2025-03-25 12:07 | 2024 | 2025-03-25 13:01 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 54 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.9 | 0.00062361 | 0.0087305 | 1206 | 1085.4
2973275 | Clear a dangerously hanging tree branch | 2022-12-14 12:26 | 2022 | 2022-12-14 15:12 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 166 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 2.7667 | 0.001917 | 0.026838 | 1049 | 2902.2333
3204478 | Sustained fault Otiende ex Langata | 2025-10-23 01:07 | 2025 | 2025-10-23 03:12 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 125 | 122.2 | 177 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 2.0833 | 0.00025458 | 0.0035642 | 177 | 368.75
2972133 | Feeder off on sustained fault | 2022-12-09 00:59 | 2022 | 2022-12-09 10:06 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 547 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 9.1167 | 0.025633 | 0.35887 | 5212 | 47516.0667
3126228 | MAGADI EX LANGATA | 2024-11-05 13:05 | 2024 | 2024-11-05 15:15 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 130 | 2812 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 2.1667 | 0.0060927 | 0.085297 | 5760 | 12480
3050286 | Sustained fault. | 2023-11-28 02:45 | 2023 | 2023-11-28 12:15 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 570 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 9.5 | 0.027214 | 0.38099 | 12066 | 114627
3126252 | Trip on fault | 2024-11-05 13:52 | 2024 | 2024-11-05 15:15 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 83 | 2864.6 | 12291 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 1.3833 | 0.0039627 | 0.055478 | 12291 | 17002.55
3050243 | Sustained fault | 2023-11-27 18:26 | 2023 | 2023-11-27 22:12 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 226 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 3.7667 | 0.01079 | 0.15106 | 12066 | 45448.6
3025909 | Sustained fault Btw AY2099 and AY195 Ngei ex Langata | 2023-08-17 16:23 | 2023 | 2023-08-17 18:06 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 103 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 1.7167 | 0.0049176 | 0.068846 | 12031 | 20653.2167
3069225 | Ndalat ex langata sustained .Informed Waweru George | 2024-02-24 08:01 | 2023 | 2024-02-24 11:06 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 185 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 3.0833 | 0.0060276 | 0.084387 | 796 | 2454.3333
2999583 | Sustained fault on Ndalat ex Langata. | 2023-04-11 04:55 | 2022 | 2023-04-11 10:58 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 363 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 6.05 | 0.011827 | 0.16558 | 724 | 4380.2
3076477 | Sustained fault | 2024-03-25 02:34 | 2023 | 2024-03-25 13:59 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE FELL ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 685 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 11.4167 | 0.022318 | 0.31246 | 837 | 9555.75
3166140 | Sustained byd 5253, Nyamweya informed. | 2025-04-21 16:59 | 2024 | 2025-04-21 18:18 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 79 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 1.3167 | 0.002574 | 0.036035 | 933 | 1228.45
2989824 | Tree branch on power line | 2023-03-06 20:06 | 2022 | 2023-03-07 10:29 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 863 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 14.3833 | 0.028118 | 0.39365 | 724 | 10413.5333
3140619 | Sustained fault on Ndalat ex Langata.Informed Waweru | 2025-01-09 17:56 | 2024 | 2025-01-09 20:35 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 159 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 2.65 | 0.0051805 | 0.072527 | 925 | 2451.25
3051556 | Sustained | 2023-12-03 08:36 | 2023 | 2023-12-03 11:31 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 175 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 2.9167 | 0.0057018 | 0.079825 | 796 | 2321.6667
3130815 | Ndalat Ex Langata Sustained, Kipchumba informed | 2024-11-25 02:05 | 2024 | 2024-11-25 10:25 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 500 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 8.3333 | 0.016291 | 0.22807 | 925 | 7708.3333
2972440 | Bamboo tree shorting line, broken jumper at Y5298 | 2022-12-10 20:24 | 2022 | 2022-12-11 15:11 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 1127 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 18.7833 | 0.07006 | 0.98084 | 33290 | 625297.1667
3093944 | Sustained fault on Soweto ex Langata byd AY 5300. Informed Ragati office. | 2024-05-29 11:45 | 2023 | 2024-05-29 17:03 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 318 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 5.3 | 0.019768 | 0.27676 | 33325 | 176622.5
3008656 | Tree branch on HT line | 2023-05-18 20:16 | 2022 | 2023-05-18 21:25 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 69 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 1.15 | 0.0042894 | 0.060051 | 33284 | 38276.6
3365040 | Sustained Fault | 2026-04-28 22:04 | 2025 | 2026-04-29 12:28 | Tree Branch on Power Line | TREE/ OBJECT CONTACT | TREE BRANCH ON POWER LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 864 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 14.4 | 0.053711 | 0.75195 | 26342 | 379324.8
3145591 | Sustained byd AY 1104 | 2025-01-30 14:01 | 2024 | 2025-01-30 17:27 | Bird Shorting line | TREE/ OBJECT CONTACT | BIRD SHORTING LV LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 206 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 3.4333 | 0.0051716 | 0.072403 | 2958 | 10155.8
3211979 | Bird shorting HT line beyond AY5198 | 2025-11-21 08:52 | 2025 | 2025-11-21 10:30 | Bird Shorting line | TREE/ OBJECT CONTACT | BIRD SHORTING MV LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 98 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 1.6333 | 0.0045924 | 0.064294 | 6310 | 10306.3333
3079593 | sustained fault | 2024-04-06 09:56 | 2023 | 2024-04-06 14:12 | Bird Shorting line | TREE/ OBJECT CONTACT | BIRD SHORTING MV LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 256 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 4.2667 | 0.015914 | 0.2228 | 33325 | 142186.6667
2946034 | Stay wire shorting with concrete poles | 2022-08-14 17:01 | 2022 | 2022-08-14 18:35 | Object on the line | TREE/ OBJECT CONTACT | OBJECT ON THE LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 94 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 1.5667 | 0.0023599 | 0.033038 | 2406 | 3769.4
2991987 | Zuku cable shorting power line | 2023-03-16 00:52 | 2022 | 2023-03-16 11:37 | Object on the line | TREE/ OBJECT CONTACT | OBJECT ON THE LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 645 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 10.75 | 0.016193 | 0.2267 | 2561 | 27530.75
3157671 | Sustained fault | 2025-03-20 12:45 | 2024 | 2025-03-20 15:44 | Object on the line | TREE/ OBJECT CONTACT | OBJECT ON THE LINE | Resolved | Nairobi | Nairobi West County | Non Programmed | 179 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.9833 | 0.0083882 | 0.11744 | 5774 | 17225.7667
3077334 | Sustained fault on Ngei ex Langata byd AY 195.Informed Nyamweya. | 2024-03-27 15:29 | 2023 | 2024-03-27 19:01 | Punctured Underground Cable | 3rd PARTY/FOREIGN INTERFERENCE | PUNCTURED UNDERGROUND CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 212 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 3.5333 | 0.010122 | 0.1417 | 12107 | 42778.0667
3229434 | A trip on Ndalat ex Langata awaiting operator Informed Lunali | 2026-01-14 11:40 | 2025 | 2026-01-14 14:04 | Punctured Underground Cable | 3rd PARTY/FOREIGN INTERFERENCE | PUNCTURED UNDERGROUND CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 144 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 2.4 | 0.0046918 | 0.065685 | 988 | 2371.2
3214994 | Sustained fault | 2025-12-04 13:15 | 2025 | 2025-12-04 19:30 | Punctured Underground Cable | 3rd PARTY/FOREIGN INTERFERENCE | PUNCTURED UNDERGROUND CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 375 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 6.25 | 0.023312 | 0.32637 | 27872 | 174200
3016938 | Hardy ex Langata controlled to replace broken HT pole hit by lorry beyond ABS Y5 | 2023-06-29 18:09 | 2022 | 2023-06-29 19:07 | Knocked Pole | 3rd PARTY/FOREIGN INTERFERENCE | KNOCKED POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 58 | 1506.3 | 2652 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.96667 | 0.0014561 | 0.020385 | 2652 | 2563.6
3255732 | Sustained fault | 2026-03-04 12:55 | 2025 | 2026-03-04 14:32 | Knocked Pole | 3rd PARTY/FOREIGN INTERFERENCE | KNOCKED POLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 97 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 1.6167 | 0.0031604 | 0.044246 | 988 | 1597.2667
3124611 | Magadi rd ex Langata sustained,CB to 100.Informed Nyamweya. | 2024-10-29 09:47 | 2024 | 2024-10-29 16:56 | O/HEAD Interferance | 3rd PARTY/FOREIGN INTERFERENCE | O/HEAD LINE INTERFERANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 429 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 7.15 | 0.020104 | 0.28145 | 5760 | 41184
2995163 | Controlled | 2023-03-27 20:44 | 2022 | 2023-03-28 12:55 | O/HEAD Interferance | 3rd PARTY/FOREIGN INTERFERENCE | O/HEAD LINE INTERFERANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 971 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 16.1833 | 0.060362 | 0.84507 | 33290 | 538743.1667
3099848 | sustained | 2024-06-27 02:33 | 2023 | 2024-06-27 09:57 | Other | OTHERS (Non-Breakdown Related) | OTHER CAUSE | Resolved | Nairobi | Nairobi West County | Non Programmed | 444 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 7.4 | 0.011147 | 0.15605 | 2832 | 20956.8
3155709 | Overload | 2025-03-13 19:12 | 2024 | 2025-03-13 22:49 | Other | OTHERS (Non-Breakdown Related) | OTHER CAUSE | Resolved | Nairobi | Nairobi West County | Non Programmed | 216 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 3.6 | 0.013428 | 0.18799 | 31280 | 112608
3025505 | Fire incident near Clean shelf Supermarket | 2023-08-15 16:16 | 2023 | 2023-08-15 17:17 | Reportable Electrical Incidence | OTHERS (Non-Breakdown Related) | FIRE INCIDENCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 61 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 1.0167 | 0.0029123 | 0.040773 | 12031 | 12231.5167
3230568 | Fire incident at Karanja Rd | 2026-01-17 14:12 | 2025 | 2026-01-17 15:52 | Reportable Electrical Incidence | OTHERS (Non-Breakdown Related) | FIRE INCIDENCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 100 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 1.6667 | 0.0062165 | 0.087031 | 27872 | 46453.3333
3013183 | Soweto ex Langata controlled due to fire incident at Kibera drive. | 2023-06-11 01:30 | 2022 | 2023-06-11 11:30 | Reportable Electrical Incidence | OTHERS (Non-Breakdown Related) | FIRE INCIDENCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 600 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 10 | 0.037299 | 0.52219 | 33284 | 332840
3303175 | Under Frequency | 2026-04-02 11:53 | 2025 | 2026-04-02 12:26 | Under frequency | LOSS OF SUPPLY | UNDER FREQUENCY | Resolved | Nairobi | Nairobi West County | Non Programmed | 33 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.55 | 0.0020514 | 0.02872 | 27892 | 15340.6
3029883 | Underfrequency operation due to loss of generation | 2023-09-06 18:37 | 2023 | 2023-09-06 20:43 | Under frequency | LOSS OF SUPPLY | UNDER FREQUENCY | Resolved | Nairobi | Nairobi West County | Non Programmed | 126 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 2.1 | 0.0078328 | 0.10966 | 33295 | 69919.5
3190646 | Underfrequency operation due to loss of UETCL import | 2025-08-19 19:39 | 2025 | 2025-08-19 19:55 | Under frequency | LOSS OF SUPPLY | UNDER FREQUENCY | Resolved | Nairobi | Nairobi West County | Non Programmed | 16 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.26667 | 0.00099464 | 0.013925 | 27872 | 7432.5333
3216112 | Loss of wind generation | 2025-12-09 19:07 | 2025 | 2025-12-09 21:57 | Under frequency | LOSS OF SUPPLY | UNDER FREQUENCY | Resolved | Nairobi | Nairobi West County | Non Programmed | 170 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 2.8333 | 0.010568 | 0.14795 | 27872 | 78970.6667
2985683 | controlled | 2023-02-15 14:55 | 2022 | 2023-02-15 15:58 | Under frequency | LOSS OF SUPPLY | UNDER FREQUENCY | Resolved | Nairobi | Nairobi West County | Non Programmed | 63 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 1.05 | 0.0039164 | 0.05483 | 33290 | 34954.5
2962582 | Sustained fault on Hardy ex Langata | 2022-10-30 14:08 | 2022 | 2022-10-30 19:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 293 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 4.8833 | 0.0073558 | 0.10298 | 2561 | 12506.2167
3017399 | Transient fault | 2023-07-02 09:19 | 2023 | 2023-07-02 20:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 651 | 1506.3 | 2652 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 10.85 | 0.016343 | 0.22881 | 2652 | 28774.2
3016897 | Transient fault | 2023-06-29 15:23 | 2022 | 2023-06-29 15:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2652 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.033333 | 5.021e-05 | 0.00070294 | 2652 | 88.4
2962405 | Trip on fault | 2022-10-29 16:03 | 2022 | 2022-10-29 16:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 38 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.63333 | 0.00095399 | 0.013356 | 2561 | 1621.9667
3154388 | Transient fault | 2025-03-09 15:23 | 2024 | 2025-03-09 15:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 16 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.26667 | 0.00040168 | 0.0056235 | 2964 | 790.4
3300160 | Transient fault | 2026-03-31 18:40 | 2025 | 2026-03-31 18:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.2 | 0.0004033 | 0.0056462 | 3056 | 611.2
3352304 | sustained fault | 2026-04-19 18:58 | 2025 | 2026-04-19 20:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 94 | 4828.2 | 2971 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 1.5667 | 0.0075642 | 0.1059 | 2971 | 4654.5667
3299663 | Transient fault | 2026-03-31 10:56 | 2025 | 2026-03-31 11:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.066667 | 0.00013443 | 0.0018821 | 3056 | 203.7333
3299702 | Transient fault | 2026-03-31 12:43 | 2025 | 2026-03-31 12:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.1 | 0.00020165 | 0.0028231 | 3056 | 305.6
3104300 | Transient fault | 2024-07-19 12:09 | 2024 | 2024-07-19 12:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.033333 | 5.021e-05 | 0.00070294 | 2832 | 94.4
3140990 | Sustained fault | 2025-01-11 17:38 | 2024 | 2025-01-11 18:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.83333 | 0.0012553 | 0.017573 | 2958 | 2465
3165825 | Transient fault | 2025-04-20 15:08 | 2024 | 2025-04-20 15:15 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.11667 | 0.00017573 | 0.0024603 | 2964 | 345.8
3165838 | Sustained fault on Hardy ex Langata, Nyamweya informed. | 2025-04-20 15:06 | 2024 | 2025-04-20 20:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 316 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 5.2667 | 0.0079332 | 0.11106 | 2964 | 15610.4
3053028 | Transient fault | 2023-12-09 23:53 | 2023 | 2023-12-09 23:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 32 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.53333 | 0.00080336 | 0.011247 | 2807 | 1497.0667
2940767 | Transient fault | 2022-07-20 14:50 | 2022 | 2022-07-20 14:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.083333 | 0.00012553 | 0.0017573 | 2406 | 200.5
3227151 | A trip on Hardy ex Langata | 2026-01-07 09:47 | 2025 | 2026-01-07 10:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 34 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.56667 | 0.0011427 | 0.015998 | 3000 | 1700
3235177 | A trip on Hardy ex Langata | 2026-01-29 21:54 | 2025 | 2026-01-29 22:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.83333 | 0.0016804 | 0.023526 | 3000 | 2500
3243699 | Sustained fault | 2026-02-14 21:46 | 2025 | 2026-02-14 22:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 69 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.15 | 0.002319 | 0.032466 | 3000 | 3450
3218329 | Transient fault | 2025-12-17 23:48 | 2025 | 2025-12-17 23:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.033333 | 6.7217e-05 | 0.00094103 | 3000 | 100
3218310 | Transient fault | 2025-12-17 20:15 | 2025 | 2025-12-17 20:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.05 | 0.00010082 | 0.0014115 | 3000 | 150
3227637 | Repair broken dropper at s/s 0449 | 2026-01-08 13:43 | 2025 | 2026-01-08 14:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 60 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 1 | 0.0020165 | 0.028231 | 3000 | 3000
3256965 | Trip on fault | 2026-03-06 07:26 | 2025 | 2026-03-06 08:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.83333 | 0.0016804 | 0.023526 | 3000 | 2500
3244200 | Sustained fault | 2026-02-15 22:30 | 2025 | 2026-02-16 00:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 103 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.7167 | 0.0034617 | 0.048463 | 3000 | 5150
3192149 | Transient fault | 2025-08-29 03:46 | 2025 | 2025-08-29 03:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.05 | 0.00010082 | 0.0014115 | 3000 | 150
3219741 | Transient fault | 2025-12-21 11:07 | 2025 | 2025-12-21 11:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.18333 | 0.00036969 | 0.0051757 | 3000 | 550
3054379 | Transient fault | 2023-12-16 09:19 | 2023 | 2023-12-16 09:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 5.021e-05 | 0.00070294 | 2807 | 93.5667
3072776 | Transient fault | 2024-03-09 16:46 | 2023 | 2024-03-09 16:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.21667 | 0.00032637 | 0.0045691 | 2832 | 613.6
3165541 | Unestablished fault | 2025-04-19 11:12 | 2024 | 2025-04-19 12:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 70 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 1.1667 | 0.0017573 | 0.024603 | 2964 | 3458
3185013 | Transient fault | 2025-07-23 11:38 | 2025 | 2025-07-23 11:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.083333 | 0.00016804 | 0.0023526 | 3000 | 250
3160354 | sustained fault | 2025-03-29 18:19 | 2024 | 2025-03-29 18:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 37 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.61667 | 0.00092888 | 0.013004 | 2964 | 1827.8
3160622 | Off awaiting operator | 2025-03-31 03:59 | 2024 | 2025-03-31 04:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 27 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.45 | 0.00067784 | 0.0094897 | 2964 | 1333.8
3086741 | Sustained fault | 2024-05-01 11:33 | 2023 | 2024-05-01 16:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 270 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 4.5 | 0.0067783 | 0.094897 | 2832 | 12744
3072662 | Transient fault | 2024-03-09 03:37 | 2023 | 2024-03-09 03:42 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.083333 | 0.00012553 | 0.0017573 | 2832 | 236
3069218 | Transient fault | 2024-02-24 07:41 | 2023 | 2024-02-24 07:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.05 | 7.5315e-05 | 0.0010544 | 2807 | 140.35
3055840 | Sustained fault | 2023-12-23 04:52 | 2023 | 2023-12-23 06:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 1.6 | 0.0024101 | 0.033741 | 2807 | 4491.2
3145161 | Sustained fault | 2025-01-29 09:27 | 2024 | 2025-01-29 09:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 31 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.51667 | 0.00077826 | 0.010896 | 2958 | 1528.3
3187544 | Transient fault | 2025-08-06 02:19 | 2025 | 2025-08-06 03:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 1.6 | 0.0032264 | 0.04517 | 3000 | 4800
3101447 | Transient fault | 2024-07-05 19:04 | 2024 | 2024-07-05 19:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.016667 | 2.5105e-05 | 0.00035147 | 2832 | 47.2
3086241 | Transient fault | 2024-04-29 17:44 | 2023 | 2024-04-29 17:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.2 | 0.00030126 | 0.0042176 | 2832 | 566.4
3023909 | Transient fault | 2023-08-06 20:28 | 2023 | 2023-08-06 20:42 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 0.23333 | 0.00035147 | 0.0049206 | 2654 | 619.2667
2970507 | Transient fault | 2022-12-01 08:20 | 2022 | 2022-12-01 08:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.05 | 7.5315e-05 | 0.0010544 | 2561 | 128.05
3160177 | Transient fault | 2025-03-29 06:58 | 2024 | 2025-03-29 07:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.05 | 7.5315e-05 | 0.0010544 | 2964 | 148.2
3070462 | Transient fault | 2024-02-28 19:46 | 2023 | 2024-02-28 19:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 1506.3 | 2827 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.18333 | 0.00027615 | 0.0038662 | 2827 | 518.2833
3030883 | Transient fault | 2023-09-10 18:31 | 2023 | 2023-09-10 18:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.33333 | 0.0005021 | 0.0070294 | 2654 | 884.6667
3179031 | TRANSIENT FAULT | 2025-06-20 09:38 | 2024 | 2025-06-20 09:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2016.5 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.016667 | 3.3608e-05 | 0.00047052 | 2964 | 49.4
3044586 | Transient fault | 2023-11-07 13:41 | 2023 | 2023-11-07 13:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 30 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.5 | 0.00075315 | 0.010544 | 2807 | 1403.5
3154581 | Transient fault | 2025-03-10 02:23 | 2024 | 2025-03-10 02:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.033333 | 5.021e-05 | 0.00070294 | 2964 | 98.8
3157981 | Transient fault | 2025-03-21 08:12 | 2024 | 2025-03-21 08:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.36667 | 0.00055231 | 0.0077323 | 2964 | 1086.8
3189396 | Transient fault | 2025-08-14 06:39 | 2025 | 2025-08-14 06:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.1 | 0.00020165 | 0.0028231 | 3000 | 300
3093188 | Off a waiting operator | 2024-05-26 00:54 | 2023 | 2024-05-26 07:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 416 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 6.9333 | 0.010444 | 0.14621 | 2832 | 19635.2
3091011 | Transient fault | 2024-05-16 19:27 | 2023 | 2024-05-16 19:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.05 | 7.5315e-05 | 0.0010544 | 2832 | 141.6
3044487 | Sustained fault | 2023-11-07 08:14 | 2023 | 2023-11-07 09:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 76 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 1.2667 | 0.001908 | 0.026712 | 2807 | 3555.5333
2950186 | TRANSIENT FAULT | 2022-09-03 06:29 | 2022 | 2022-09-03 06:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.033333 | 5.021e-05 | 0.00070294 | 2406 | 80.2
3056005 | Transient fault | 2023-12-20 23:56 | 2023 | 2023-12-20 23:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 5.021e-05 | 0.00070294 | 2807 | 93.5667
3020371 | TRANSIENT FAULT | 2023-07-19 12:29 | 2023 | 2023-07-19 12:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.05 | 7.5315e-05 | 0.0010544 | 2654 | 132.7
3187351 | Transient fault | 2025-08-05 03:07 | 2025 | 2025-08-05 03:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.083333 | 0.00016804 | 0.0023526 | 3000 | 250
3057816 | Transient fault | 2024-01-03 07:31 | 2023 | 2024-01-03 07:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.05 | 7.5315e-05 | 0.0010544 | 2807 | 140.35
2984758 | A trip on Kuwinda ex Langata,awaiting an operator. | 2023-02-11 17:12 | 2022 | 2023-02-11 18:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 61 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 1.0167 | 0.00097915 | 0.013708 | 1922 | 1954.0333
3023697 | Transient fault | 2023-08-05 01:12 | 2023 | 2023-08-05 01:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 0.066667 | 6.4207e-05 | 0.00089889 | 1967 | 131.1333
3365970 | A trip on Kuwinda ex Langata | 2026-04-29 13:36 | 2025 | 2026-04-29 16:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 155 | 963.1 | 1814 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 2.5833 | 0.002488 | 0.034832 | 1814 | 4686.1667
3125680 | TRANSIENT | 2024-11-03 02:13 | 2024 | 2024-11-03 02:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.05 | 4.8155e-05 | 0.00067417 | 2139 | 106.95
2984743 | Transient fault | 2023-02-11 16:24 | 2022 | 2023-02-11 16:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 963 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.21667 | 0.00020865 | 0.0029211 | 1922 | 416.4333
3172639 | A Trip on fault awaiting operator | 2025-05-19 10:17 | 2024 | 2025-05-19 12:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 114 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 1.9 | 0.0018299 | 0.025618 | 2155 | 4094.5
2964120 | Feeder off on sustained fault | 2022-11-05 13:38 | 2022 | 2022-11-05 15:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 88 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 1.4667 | 0.0014125 | 0.019776 | 1922 | 2818.9333
3078309 | Sustained fault Kuwinda ex Langata | 2024-04-01 03:24 | 2023 | 2024-04-01 10:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 417 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 6.95 | 0.0066935 | 0.09371 | 2020 | 14039
3067648 | Transient fault | 2024-02-18 13:04 | 2023 | 2024-02-18 13:07 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.05 | 4.8155e-05 | 0.00067417 | 1991 | 99.55
3068877 | Transient fault | 2024-02-22 18:37 | 2023 | 2024-02-22 18:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 80 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 1.3333 | 0.0012841 | 0.017978 | 1991 | 2654.6667
2956933 | Sustained fault | 2022-10-04 07:07 | 2022 | 2022-10-04 12:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 346 | 963.1 | 1879 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 5.7667 | 0.0055539 | 0.077754 | 1879 | 10835.5667
3266529 | Transient fault | 2026-03-14 22:56 | 2025 | 2026-03-14 23:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 1819 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.083333 | 8.0258e-05 | 0.0011236 | 1819 | 151.5833
3288043 | Transient fault | 2026-03-22 19:36 | 2025 | 2026-03-22 19:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 963.1 | 1819 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.21667 | 0.00020867 | 0.0029214 | 1819 | 394.1167
3264632 | TRANSIENT FAULT | 2026-03-14 02:27 | 2025 | 2026-03-14 02:29 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1819 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.033333 | 3.2103e-05 | 0.00044945 | 1819 | 60.6333
3222565 | A Trip on Kuwinda ex Langata awaiting operator (Vacant shift)Not closing on sca | 2025-12-29 16:39 | 2025 | 2025-12-29 17:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 65 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 1.0833 | 0.0010434 | 0.014607 | 1796 | 1945.6667
3256827 | A Trip on Kuwinda ex Langata awaiting operator | 2026-03-05 18:15 | 2025 | 2026-03-05 23:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 326 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 5.4333 | 0.0052328 | 0.07326 | 1796 | 9758.2667
3231451 | Transient fault | 2026-01-20 11:27 | 2025 | 2026-01-20 11:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.083333 | 8.0258e-05 | 0.0011236 | 1796 | 149.6667
3244209 | Transient fault | 2026-02-15 23:45 | 2025 | 2026-02-16 00:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 32 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.53333 | 0.00051365 | 0.0071911 | 1796 | 957.8667
3195821 | . | 2025-09-14 12:56 | 2025 | 2025-09-14 13:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2025 | 0.083333 | 8.0258e-05 | 0.0011236 | 1796 | 149.6667
3244211 | Sustained fault | 2026-02-16 00:26 | 2025 | 2026-02-16 13:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 802 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 13.3667 | 0.012873 | 0.18023 | 1796 | 24006.5333
3221754 | Transient fault | 2025-12-27 13:06 | 2025 | 2025-12-27 13:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 25 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.41667 | 0.00040129 | 0.0056181 | 1796 | 748.3333
2993191 | Transient fault | 2023-03-21 01:47 | 2022 | 2023-03-21 01:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.2 | 0.00019262 | 0.0026967 | 1922 | 384.4
2992093 | Transient fault | 2023-03-16 02:40 | 2022 | 2023-03-16 02:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.13333 | 0.00012841 | 0.0017978 | 1922 | 256.2667
2979626 | Transient fault | 2023-01-16 13:05 | 2022 | 2023-01-16 13:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.016667 | 1.6052e-05 | 0.00022472 | 1922 | 32.0333
2976680 | Transient fault | 2023-01-01 20:13 | 2022 | 2023-01-01 20:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.33333 | 0.00032103 | 0.0044945 | 1922 | 640.6667
3031717 | Transient fault | 2023-09-13 20:43 | 2023 | 2023-09-13 20:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.11667 | 0.00011236 | 0.0015731 | 1967 | 229.4833
3101238 | KUWINDA EX LANGATA | 2024-07-04 14:51 | 2024 | 2024-07-04 14:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1603 | 2393 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.016667 | 2.6717e-05 | 0.00037403 | 2393 | 39.8833
3048579 | A trip on Kuwinda ex Langata. SCADA offline Nyamweya informed | 2023-11-22 04:40 | 2023 | 2023-11-22 05:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 78 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 1.3 | 0.001252 | 0.017528 | 1991 | 2588.3
3045784 | A trip on Kuwinda ex Langata awaiting operator informed Mageto | 2023-11-11 16:25 | 2023 | 2023-11-11 20:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 243 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 4.05 | 0.0039006 | 0.054608 | 1991 | 8063.55
3088016 | Transient fault | 2024-05-05 11:19 | 2023 | 2024-05-05 11:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.033333 | 3.2103e-05 | 0.00044945 | 2020 | 67.3333
2998853 | Transient fault | 2023-04-06 18:16 | 2022 | 2023-04-06 18:19 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.05 | 4.8155e-05 | 0.00067417 | 1922 | 96.1
3081682 | Transient fault | 2024-04-13 16:30 | 2023 | 2024-04-13 16:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.066667 | 6.4207e-05 | 0.00089889 | 2020 | 134.6667
3059856 | Transient fault | 2024-01-13 11:40 | 2023 | 2024-01-13 11:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.18333 | 0.00017657 | 0.002472 | 1991 | 365.0167
3010021 | Transient fault | 2023-05-25 13:25 | 2022 | 2023-05-25 13:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 21 | 963.1 | 1938 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 0.35 | 0.00033708 | 0.0047192 | 1938 | 678.3
2987987 | Sustained fault on Kuwinda ex Langata | 2023-02-25 17:18 | 2022 | 2023-02-25 21:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 232 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 3.8667 | 0.003724 | 0.052136 | 1922 | 7431.7333
2937204 | KUWINDA EX LANGATA | 2022-07-04 12:56 | 2022 | 2022-07-04 12:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963 | 1879 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.033333 | 3.21e-05 | 0.0004494 | 1879 | 62.6333
3143485 | Transient fault | 2025-01-22 23:13 | 2024 | 2025-01-22 23:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.11667 | 0.00011236 | 0.0015731 | 2139 | 249.55
3037788 | Transient fault | 2023-10-10 01:01 | 2023 | 2023-10-10 01:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.033333 | 3.2103e-05 | 0.00044945 | 1967 | 65.5667
2968788 | Transient fault | 2022-11-23 16:31 | 2022 | 2022-11-23 16:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 0.066667 | 6.4207e-05 | 0.00089889 | 1922 | 128.1333
3165477 | Transient fault | 2025-04-18 20:57 | 2024 | 2025-04-18 21:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.05 | 4.8155e-05 | 0.00067417 | 2155 | 107.75
3060832 | Sustained fault | 2024-01-18 13:08 | 2023 | 2024-01-18 14:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 99 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.65 | 0.0015891 | 0.022248 | 1991 | 3285.15
2970972 | Transient fault | 2022-12-03 17:14 | 2022 | 2022-12-03 17:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.033333 | 3.2103e-05 | 0.00044945 | 1922 | 64.0667
3048577 | KUWINDA EX LANGATA | 2023-11-22 04:42 | 2023 | 2023-11-22 04:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 963 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.016667 | 1.605e-05 | 0.0002247 | 1991 | 33.1833
3048648 | KUWINDA EX LANGATA | 2023-11-22 10:30 | 2023 | 2023-11-22 10:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.033333 | 3.21e-05 | 0.0004494 | 1991 | 66.3667
3048735 | KUWINDA EX LANGATA | 2023-11-22 13:18 | 2023 | 2023-11-22 13:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.05 | 4.815e-05 | 0.0006741 | 1991 | 99.55
3055168 | Transient fault | 2023-12-20 07:03 | 2023 | 2023-12-20 07:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 3.2103e-05 | 0.00044945 | 1991 | 66.3667
3101159 | Transient fault | 2024-07-04 09:36 | 2024 | 2024-07-04 09:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.05 | 4.8155e-05 | 0.00067417 | 2020 | 101
3080947 | TRANSIENT FAULT | 2024-04-10 23:08 | 2023 | 2024-04-10 23:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.05 | 4.8155e-05 | 0.00067417 | 2020 | 101
2938022 | Transient fault | 2022-07-07 18:32 | 2022 | 2022-07-07 18:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963 | 1879 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.033333 | 3.21e-05 | 0.0004494 | 1879 | 62.6333
3057809 | Transient Fault | 2024-01-03 06:50 | 2023 | 2024-01-03 06:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.083333 | 8.0258e-05 | 0.0011236 | 1991 | 165.9167
3125986 | Tranisient fault | 2024-11-04 14:42 | 2024 | 2024-11-04 14:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.083333 | 8.0258e-05 | 0.0011236 | 2139 | 178.25
3174582 | KUWINDA EX LANGATA | 2025-05-28 17:28 | 2024 | 2025-05-28 17:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 963 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0 | 0 | 0 | 2155 | 0
3148197 | Transient fault | 2025-02-11 14:05 | 2024 | 2025-02-11 14:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.18333 | 0.00017657 | 0.002472 | 2139 | 392.15
3166486 | KUWINDA EX LANGATA | 2025-04-23 00:08 | 2024 | 2025-04-23 00:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.033333 | 3.21e-05 | 0.0004494 | 2155 | 71.8333
3134793 | Transient fault | 2024-12-10 16:48 | 2024 | 2024-12-10 16:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.05 | 4.8155e-05 | 0.00067417 | 2139 | 106.95
3166131 | Transient fault | 2025-04-21 16:59 | 2024 | 2025-04-21 17:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.15 | 0.00014447 | 0.0020225 | 2155 | 323.25
3019863 | Transient fault | 2023-07-16 16:55 | 2023 | 2023-07-16 16:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.05 | 4.8155e-05 | 0.00067417 | 1967 | 98.35
3090969 | Kuwinda ex Langata off awaiting operator, Mageto informed. | 2024-05-16 17:41 | 2023 | 2024-05-16 18:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 68 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 1.1333 | 0.0010915 | 0.015281 | 2020 | 2289.3333
3021660 | Transient fault | 2023-07-25 18:41 | 2023 | 2023-07-25 18:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.033333 | 3.2103e-05 | 0.00044945 | 1967 | 65.5667
3092927 | Kuwinda ex Langata off awaiting operator, Waweru informed. | 2024-05-24 15:11 | 2023 | 2024-05-24 16:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 1.1167 | 0.0010755 | 0.015056 | 2020 | 2255.6667
3124845 | Trace maintenance | 2024-10-30 09:21 | 2024 | 2024-10-30 17:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 499 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 8.3167 | 0.0080098 | 0.11214 | 2139 | 17789.35
2967068 | Transient fault | 2022-11-17 11:14 | 2022 | 2022-11-17 11:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 0.033333 | 3.2103e-05 | 0.00044945 | 1922 | 64.0667
3135695 | Transient fault | 2024-12-15 02:28 | 2024 | 2024-12-15 03:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 79 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 1.3167 | 0.0012681 | 0.017753 | 2139 | 2816.35
3046566 | Transient fault | 2023-11-14 18:41 | 2023 | 2023-11-14 18:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.083333 | 8.0258e-05 | 0.0011236 | 1991 | 165.9167
3043629 | Trip on fault | 2023-11-03 22:32 | 2023 | 2023-11-04 10:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 711 | 692.9 | 1066 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 11.85 | 0.0082109 | 0.11495 | 1066 | 12632.1
3154079 | transient | 2025-03-07 21:31 | 2024 | 2025-03-07 21:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.083333 | 5.7742e-05 | 0.00080838 | 1206 | 100.5
3062934 | Transient fault | 2024-01-28 10:47 | 2023 | 2024-01-28 10:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 692.9 | 1081 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.033333 | 2.3097e-05 | 0.00032335 | 1081 | 36.0333
2984158 | Feeder off on sustained fault | 2023-02-08 12:07 | 2022 | 2023-02-08 13:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 66 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 1.1 | 0.00076219 | 0.010671 | 1049 | 1153.9
3014938 | Sustained fault on Karen Hospital ex Langata. | 2023-06-19 13:46 | 2022 | 2023-06-19 19:53 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 367 | 692.9 | 1059 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 6.1167 | 0.0042382 | 0.059335 | 1059 | 6477.55
3069564 | Transient fault | 2024-02-25 13:40 | 2023 | 2024-02-25 14:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 692.9 | 1081 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.33333 | 0.00023097 | 0.0032335 | 1081 | 360.3333
2994096 | Transient fault | 2023-03-24 01:26 | 2022 | 2023-03-24 01:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.11667 | 8.0838e-05 | 0.0011317 | 1049 | 122.3833
3200615 | TRANSIENT FAULT | 2025-10-05 19:09 | 2025 | 2025-10-05 19:19 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 0 | 0 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.16667 | 0 | 0 | 0 | 0
3234353 | Sustained fault | 2026-01-27 18:59 | 2025 | 2026-01-27 20:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 0 | 1097 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 1.6 | 0 | 0 | 1097 | 1755.2
3205867 | Transient fault | 2025-10-28 09:14 | 2025 | 2025-10-28 09:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 0 | 1097 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.21667 | 0 | 0 | 1097 | 237.6833
3190315 | Transient fault | 2025-08-18 06:25 | 2025 | 2025-08-18 06:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 0 | 0 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.033333 | 0 | 0 | 0 | 0
3182136 | Transient fault | 2025-07-07 15:21 | 2025 | 2025-07-07 15:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.083333 | 7.1183e-05 | 0.00099657 | 1206 | 100.5
3043434 | Transient | 2023-11-03 02:13 | 2023 | 2023-11-03 02:15 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 692.9 | 1066 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.033333 | 2.3097e-05 | 0.00032335 | 1066 | 35.5333
3128778 | Transient fault | 2024-11-15 13:56 | 2024 | 2024-11-15 14:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 18 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.3 | 0.00020787 | 0.0029102 | 1188 | 356.4
3040393 | Transient fault | 2023-10-20 19:53 | 2023 | 2023-10-20 19:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1066 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.05 | 3.4645e-05 | 0.00048503 | 1066 | 53.3
3160401 | Off awaiting operator | 2025-03-30 00:43 | 2024 | 2025-03-30 00:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.15 | 0.00010394 | 0.0014551 | 1206 | 180.9
2951129 | Transient fault | 2022-09-07 09:08 | 2022 | 2022-09-07 10:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 97 | 692.9 | 872 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 1.6167 | 0.0011202 | 0.015683 | 872 | 1409.7333
3103781 | off | 2024-07-17 10:46 | 2024 | 2024-07-17 13:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 178 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 2.9667 | 0.0020556 | 0.028778 | 1092 | 3239.6
3105263 | Transient fault | 2024-07-25 03:41 | 2024 | 2024-07-25 03:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.066667 | 4.6193e-05 | 0.00064671 | 1092 | 72.8
3123563 | Transient fault | 2024-10-23 17:28 | 2024 | 2024-10-23 17:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 15 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 0.25 | 0.00017322 | 0.0024252 | 1188 | 297
3115367 | Transient fault | 2024-09-17 15:59 | 2024 | 2024-09-17 16:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.28333 | 0.00019632 | 0.0027485 | 1092 | 309.4
3127769 | Transient fault | 2024-11-12 07:28 | 2024 | 2024-11-12 07:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.033333 | 2.3097e-05 | 0.00032335 | 1188 | 39.6
3069038 | Sustained fault on Karen hospital ex Langata. Gikera informed | 2024-02-23 13:03 | 2023 | 2024-02-23 13:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 692.9 | 1081 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0 | 0 | 0 | 1081 | 0
3085759 | Transient fault | 2024-04-27 20:24 | 2023 | 2024-04-27 20:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0 | 0 | 0 | 1092 | 0
3041557 | Transient fault | 2023-10-26 14:31 | 2023 | 2023-10-26 14:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 692.9 | 1066 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.033333 | 2.3097e-05 | 0.00032335 | 1066 | 35.5333
3132832 | TRANSIENT FAULT | 2024-12-02 06:10 | 2024 | 2024-12-02 06:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.05 | 3.4645e-05 | 0.00048503 | 1188 | 59.4
3165478 | Transient fault | 2025-04-18 20:57 | 2024 | 2025-04-18 21:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.05 | 3.4645e-05 | 0.00048503 | 1206 | 60.3
3160174 | Transient fault | 2025-03-29 05:55 | 2024 | 2025-03-29 05:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.066667 | 4.6193e-05 | 0.00064671 | 1206 | 80.4
3173614 | Transient fault | 2025-05-23 17:02 | 2024 | 2025-05-23 17:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.066667 | 5.6947e-05 | 0.00079725 | 1206 | 80.4
2936930 | Transient fault | 2022-07-03 10:50 | 2022 | 2022-07-03 10:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 692.9 | 872 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.083333 | 5.7742e-05 | 0.00080838 | 872 | 72.6667
3157076 | Transient fault | 2025-03-18 11:08 | 2024 | 2025-03-18 11:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 33 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.55 | 0.0003811 | 0.0053353 | 1206 | 663.3
3011953 | Transient fault | 2023-06-04 17:38 | 2022 | 2023-06-04 17:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1059 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.05 | 3.4645e-05 | 0.00048503 | 1059 | 52.95
3179327 | Transient fault | 2025-06-22 01:28 | 2024 | 2025-06-22 01:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 19 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.31667 | 0.0002705 | 0.003787 | 1206 | 381.9
2996475 | Transient fault | 2023-03-31 18:20 | 2022 | 2023-03-31 18:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.066667 | 4.6193e-05 | 0.00064671 | 1049 | 69.9333
3015693 | Transient fault | 2023-06-22 20:17 | 2022 | 2023-06-22 20:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 692.9 | 1076 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.11667 | 8.0838e-05 | 0.0011317 | 1076 | 125.5333
2936838 | Transient fault | 2022-07-02 12:22 | 2022 | 2022-07-02 12:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 692.9 | 872 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.033333 | 2.3097e-05 | 0.00032335 | 872 | 29.0667
3133518 | TRANSIENT FAULT | 2024-12-04 20:51 | 2024 | 2024-12-04 20:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.05 | 3.4645e-05 | 0.00048503 | 1188 | 59.4
3166142 | Sustained byd 122Nyamweya informed. | 2025-04-21 16:59 | 2024 | 2025-04-22 19:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1569 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 26.15 | 0.018119 | 0.25367 | 1206 | 31536.9
3096138 | TRANSIENT FAULT | 2024-06-08 17:20 | 2023 | 2024-06-08 17:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 0.05 | 3.4645e-05 | 0.00048503 | 1092 | 54.6
3171451 | A trip on Karen Hospital ex Langata | 2025-05-13 18:54 | 2024 | 2025-05-13 21:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 181 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 3.0167 | 0.0025768 | 0.036076 | 1206 | 3638.1
3210546 | Transient fault | 2025-11-15 05:20 | 2025 | 2025-11-15 05:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 0 | 0 | 208003125 | ICOLO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.033333 | 0 | 0 | 0 | 0
3237551 | Transient fault | 2026-02-04 07:10 | 2025 | 2026-02-04 07:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 0 | 0 | 208003125 | ICOLO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.033333 | 0 | 0 | 0 | 0
3112701 | Transient fault | 2024-09-04 06:07 | 2024 | 2024-09-04 06:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 121.4 | 245 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.033333 | 4.0467e-06 | 5.6653e-05 | 245 | 8.1667
3133634 | Transient fault | 2024-12-05 09:34 | 2024 | 2024-12-05 09:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 121.4 | 241 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.083333 | 1.0117e-05 | 0.00014163 | 241 | 20.0833
3143326 | MAGADI EX LANGATA | 2025-01-22 13:35 | 2024 | 2025-01-22 16:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 188 | 2812 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 3.1333 | 0.0088109 | 0.12335 | 5760 | 18048
2989591 | Transient fault | 2023-03-05 14:02 | 2022 | 2023-03-05 14:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.016667 | 4.6862e-05 | 0.00065606 | 5212 | 86.8667
3112458 | MAGADI EX LANGATA | 2024-09-03 06:28 | 2024 | 2024-09-03 06:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2812 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.033333 | 9.3733e-05 | 0.0013123 | 5690 | 189.6667
2972066 | Transient fault | 2022-12-08 14:15 | 2022 | 2022-12-08 14:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.05 | 0.00014059 | 0.0019682 | 5212 | 260.6
3154443 | MAGADI EX LANGATA | 2025-03-09 18:29 | 2024 | 2025-03-09 19:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.1167 | 0.0031401 | 0.043961 | 5774 | 6447.6333
3152615 | MAGADI EX LANGATA | 2025-03-01 13:36 | 2024 | 2025-03-01 13:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.15 | 0.0004218 | 0.0059052 | 5774 | 866.1
3355204 | A trip on Magadi feeder | 2026-04-22 08:06 | 2025 | 2026-04-22 08:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 2811.7 | 6752 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.83333 | 0.0023431 | 0.032803 | 6752 | 5626.6667
3298907 | Magadi ex Langata sustained, Lunani informed. | 2026-03-30 18:31 | 2025 | 2026-03-31 15:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1264 | 2811.7 | 6841 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 21.0667 | 0.059233 | 0.82926 | 6841 | 144117.0667
3340208 | Transient fault | 2026-04-11 11:33 | 2025 | 2026-04-11 11:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 2811.7 | 6841 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.11667 | 0.00032803 | 0.0045924 | 6841 | 798.1167
3149964 | Transient fault | 2025-02-19 12:14 | 2024 | 2025-02-19 12:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.05 | 0.00014059 | 0.0019682 | 5774 | 288.7
3143111 | Transient fault | 2025-01-21 14:35 | 2024 | 2025-01-21 14:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 5760 | 192
2946884 | Transient fault | 2022-08-18 08:28 | 2022 | 2022-08-18 08:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.1 | 0.00028117 | 0.0039364 | 5016 | 501.6
3166135 | Transient fault | 2025-04-21 16:33 | 2024 | 2025-04-21 17:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 54 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.9 | 0.0025305 | 0.035427 | 5774 | 5196.6
3159664 | MAGADI EX LANGATA | 2025-03-27 09:46 | 2024 | 2025-03-27 09:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.033333 | 9.3733e-05 | 0.0013123 | 5774 | 192.4667
3160860 | Transient fault | 2025-03-31 17:00 | 2024 | 2025-03-31 17:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.083333 | 0.00023431 | 0.0032803 | 5774 | 481.1667
3042103 | Transient fault | 2023-10-29 15:24 | 2023 | 2023-10-29 15:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.033333 | 9.3723e-05 | 0.0013121 | 5260 | 175.3333
3138202 | MAGADI EX LANGATA | 2024-12-26 11:46 | 2024 | 2024-12-26 11:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 2812 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.16667 | 0.00046867 | 0.0065613 | 5760 | 960
3103222 | Sustained fault on Magadi ex Langata. Informed Siriba. | 2024-07-14 17:10 | 2024 | 2024-07-14 19:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 131 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 2.1833 | 0.0061389 | 0.085944 | 5690 | 12423.1667
2955473 | Transient fault | 2022-09-27 08:38 | 2022 | 2022-09-27 08:42 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.066667 | 0.00018745 | 0.0026243 | 5016 | 334.4
3209995 | Sustained fault | 2025-11-12 22:06 | 2025 | 2025-11-13 00:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 147 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 2.45 | 0.0068887 | 0.096441 | 6310 | 15459.5
3244324 | Transient fault | 2026-02-16 06:40 | 2025 | 2026-02-16 07:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.36667 | 0.001031 | 0.014433 | 6310 | 2313.6667
3257880 | Sustained fault | 2026-03-06 18:58 | 2025 | 2026-03-06 18:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0 | 0 | 0 | 6310 | 0
3249081 | A trip on Magadi ex Langat awaiting operator, SCADA offline Station unmanned, Lu | 2026-02-23 16:26 | 2025 | 2026-02-23 18:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 118 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.9667 | 0.0055297 | 0.077415 | 6310 | 12409.6667
3245221 | A Trip on Magadi ex Langat awaiting operator scada offline (Vacant shift)C | 2026-02-17 18:21 | 2025 | 2026-02-17 21:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 160 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 2.6667 | 0.0074979 | 0.10497 | 6310 | 16826.6667
3219589 | Transient fault | 2025-12-21 08:17 | 2025 | 2025-12-21 09:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 95 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 1.5833 | 0.0044519 | 0.062326 | 6310 | 9990.8333
3193031 | TRANSIENT FAULT | 2025-09-01 10:23 | 2025 | 2025-09-01 10:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2025 | 0.05 | 0.00014059 | 0.0019682 | 6310 | 315.5
3114646 | Transient fault | 2024-09-13 13:50 | 2024 | 2024-09-13 14:19 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 29 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.48333 | 0.001359 | 0.019026 | 5690 | 2750.1667
3128587 | Magadi ex Langata sustained byd ARY 5230 | 2024-11-15 02:52 | 2024 | 2024-11-15 10:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 458 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 7.6333 | 0.021463 | 0.30048 | 5760 | 43968
2983562 | Transient fault | 2023-02-05 16:16 | 2022 | 2023-02-05 16:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2812 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.016667 | 4.6867e-05 | 0.00065613 | 5212 | 86.8667
3129406 | Transient fault | 2024-11-19 03:02 | 2024 | 2024-11-19 03:07 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.083333 | 0.00023431 | 0.0032803 | 5760 | 480
2971963 | Transient fault | 2022-12-08 09:48 | 2022 | 2022-12-08 09:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.033333 | 9.3723e-05 | 0.0013121 | 5212 | 173.7333
3006625 | A trip on Magadi Rd ex Langata. CB not closing on SCADA, awaiting an operator. | 2023-05-09 07:31 | 2022 | 2023-05-09 09:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 122 | 2811.7 | 5239 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 2.0333 | 0.0057171 | 0.08004 | 5239 | 10652.6333
3020547 | Transient fault | 2023-07-20 08:15 | 2023 | 2023-07-20 08:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.016667 | 4.6862e-05 | 0.00065606 | 5260 | 87.6667
2954649 | Transient fault | 2022-09-23 10:32 | 2022 | 2022-09-23 10:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.033333 | 9.3723e-05 | 0.0013121 | 5016 | 167.2
3182707 | Transient fault | 2025-07-10 14:25 | 2025 | 2025-07-10 14:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 5774 | 192.4667
2972631 | Transient fault | 2022-12-12 08:23 | 2022 | 2022-12-12 08:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.066667 | 0.00018745 | 0.0026243 | 5212 | 347.4667
2949986 | Transient fault | 2022-09-01 18:09 | 2022 | 2022-09-01 18:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.05 | 0.00014059 | 0.0019682 | 5016 | 250.8
3152715 | TRANSIENT FAULT | 2025-03-01 17:55 | 2024 | 2025-03-01 18:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.11667 | 0.00032803 | 0.0045924 | 5774 | 673.6333
3117296 | Transient fault | 2024-09-26 12:01 | 2024 | 2024-09-26 12:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.066667 | 0.00018745 | 0.0026243 | 5760 | 384
3046361 | MAGADI EX LANGATA | 2023-11-14 10:10 | 2023 | 2023-11-14 10:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 2812 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.16667 | 0.00046867 | 0.0065613 | 5343 | 890.5
3147734 | Transient fault | 2025-02-09 14:34 | 2024 | 2025-02-09 14:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.21667 | 0.0006092 | 0.0085288 | 5760 | 1248
3149340 | Transient fault | 2025-02-16 14:49 | 2024 | 2025-02-16 15:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.85 | 0.0023899 | 0.033459 | 5760 | 4896
3066769 | Transient fault | 2024-02-14 16:25 | 2023 | 2024-02-14 16:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.2 | 0.00056234 | 0.0078728 | 5343 | 1068.6
3181469 | MAGADI EX LANGATA | 2025-07-03 09:06 | 2025 | 2025-07-03 09:07 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.016667 | 4.6867e-05 | 0.00065613 | 5774 | 96.2333
3181731 | MAGADI EX LANGATA | 2025-07-04 16:16 | 2025 | 2025-07-04 16:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.016667 | 4.6862e-05 | 0.00065606 | 5774 | 96.2333
3031546 | Transient fault | 2023-09-13 10:12 | 2023 | 2023-09-13 10:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 2812 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.33333 | 0.00093733 | 0.013123 | 5260 | 1753.3333
3070975 | Transient fault | 2024-03-02 06:55 | 2023 | 2024-03-02 06:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5674 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.033333 | 9.3723e-05 | 0.0013121 | 5674 | 189.1333
3169498 | MAGADI EX LANGATA | 2025-05-06 10:54 | 2024 | 2025-05-06 10:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.016667 | 4.6867e-05 | 0.00065613 | 5774 | 96.2333
3149265 | Transient fault | 2025-02-15 13:03 | 2024 | 2025-02-15 13:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.05 | 0.00014059 | 0.0019682 | 5760 | 288
3040313 | MAGADI EX LANGATA | 2023-10-20 14:05 | 2023 | 2023-10-20 14:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2812 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.016667 | 4.6867e-05 | 0.00065613 | 5260 | 87.6667
3166209 | Transient fault | 2025-04-21 21:19 | 2024 | 2025-04-21 21:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.066667 | 0.00018745 | 0.0026243 | 5774 | 384.9333
3132709 | Sustained fault, Nyaweya informed | 2024-12-01 17:20 | 2024 | 2024-12-01 20:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 210 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 3.5 | 0.0098409 | 0.13777 | 5760 | 20160
3164247 | MAGADI EX LANGATA | 2025-04-14 09:11 | 2024 | 2025-04-14 09:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0 | 0 | 0 | 5774 | 0
3055948 | Transient | 2023-12-23 15:37 | 2023 | 2023-12-23 15:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.05 | 0.00014059 | 0.0019682 | 5343 | 267.15
3148003 | Transient fault | 2025-02-10 14:32 | 2024 | 2025-02-10 14:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 5760 | 192
3160507 | Transient fault | 2025-03-30 12:40 | 2024 | 2025-03-30 12:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.083333 | 0.00023431 | 0.0032803 | 5774 | 481.1667
2965805 | Transient fault | 2022-11-12 13:02 | 2022 | 2022-11-12 13:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 0.016667 | 4.6862e-05 | 0.00065606 | 5212 | 86.8667
3040346 | Sustained fault | 2023-10-20 15:11 | 2023 | 2023-10-20 16:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 104 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 1.7333 | 0.0048736 | 0.068231 | 5260 | 9117.3333
3084104 | sustained | 2024-04-22 17:05 | 2023 | 2024-04-22 21:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 266 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 4.4333 | 0.012465 | 0.17451 | 5690 | 25225.6667
3129425 | MAGADI EX LANGATA | 2024-11-19 08:18 | 2024 | 2024-11-19 13:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 341 | 2978 | 5871 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 5.6833 | 0.016925 | 0.23695 | 5871 | 33366.85
3083494 | Transient fault | 2024-04-20 10:25 | 2023 | 2024-04-20 10:29 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.066667 | 0.00018745 | 0.0026243 | 5690 | 379.3333
3175088 | MAGADI EX LANGATA | 2025-05-31 01:28 | 2024 | 2025-05-31 01:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.083333 | 0.00023433 | 0.0032807 | 5774 | 481.1667
3176291 | MAGADI EX LANGATA | 2025-06-07 09:27 | 2024 | 2025-06-07 12:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 156 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 2.6 | 0.0073112 | 0.10236 | 5774 | 15012.4
3288527 | Magadi ex Langata sustsined byd AY 5198, Siriba informed. | 2026-03-23 12:13 | 2025 | 2026-03-23 12:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 38 | 2811.7 | 6841 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.63333 | 0.0017807 | 0.02493 | 6841 | 4332.6333
3070246 | Feeder off on sustained fault | 2024-02-28 09:30 | 2023 | 2024-02-28 14:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 286 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 4.7667 | 0.013402 | 0.18763 | 5343 | 25468.3
3061499 | Transient fault | 2024-01-21 10:52 | 2023 | 2024-01-21 11:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.28333 | 0.00079665 | 0.011153 | 5343 | 1513.85
3085286 | Transient fault | 2024-04-25 20:39 | 2023 | 2024-04-25 20:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.033333 | 9.3723e-05 | 0.0013121 | 5690 | 189.6667
3017157 | transient fault | 2023-06-30 19:13 | 2022 | 2023-06-30 19:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 2811.7 | 5258 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.11667 | 0.00032803 | 0.0045924 | 5258 | 613.4333
3209860 | Transient fault | 2025-11-12 09:03 | 2025 | 2025-11-12 09:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 6310 | 210.3333
3175266 | Transien fault | 2025-06-01 06:16 | 2024 | 2025-06-01 06:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 19 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.31667 | 0.00089037 | 0.012465 | 5774 | 1828.4333
3020568 | Transient fault | 2023-07-20 11:01 | 2023 | 2023-07-20 11:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.016667 | 4.6862e-05 | 0.00065606 | 5260 | 87.6667
3003853 | Transient fault. | 2023-04-26 18:22 | 2022 | 2023-04-26 18:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5239 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.05 | 0.00014059 | 0.0019682 | 5239 | 261.95
2994650 | Transient fault | 2023-03-26 04:50 | 2022 | 2023-03-26 05:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 58 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.96667 | 0.002718 | 0.038052 | 5212 | 5038.2667
3060663 | Magadi ex Langata off awaiting operator,Waweru informed | 2024-01-17 15:59 | 2023 | 2024-01-17 17:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 75 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.25 | 0.0035146 | 0.049205 | 5343 | 6678.75
3015821 | TRANSIENT FAULT | 2023-06-23 11:04 | 2022 | 2023-06-23 11:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5258 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.033333 | 9.3723e-05 | 0.0013121 | 5258 | 175.2667
3020573 | Feeder off on sustained fault | 2023-07-20 12:00 | 2023 | 2023-07-20 13:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 108 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 1.8 | 0.0050611 | 0.070855 | 5260 | 9468
3160599 | Transient fault | 2025-03-30 19:00 | 2024 | 2025-03-30 19:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 5774 | 192.4667
3148180 | MAGADI EX LANGATA | 2025-02-11 15:05 | 2024 | 2025-02-13 15:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2881 | 2812 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 48.0167 | 0.13502 | 1.8903 | 5760 | 276576
3034220 | MAGADI EX LANGATA | 2023-09-24 17:30 | 2023 | 2023-09-24 17:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2812 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.016667 | 4.6867e-05 | 0.00065613 | 5260 | 87.6667
3130943 | Sustained fault | 2024-11-25 13:30 | 2024 | 2024-11-25 15:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 120 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 2 | 0.0056234 | 0.078728 | 5760 | 11520
3175341 | Transient fault | 2025-06-01 14:19 | 2024 | 2025-06-01 14:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.033333 | 9.3723e-05 | 0.0013121 | 5774 | 192.4667
2957015 | Transient fault | 2022-10-04 08:14 | 2022 | 2022-10-04 08:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.1 | 0.00028117 | 0.0039364 | 5016 | 501.6
3012900 | Transient fault | 2023-06-09 10:14 | 2022 | 2023-06-09 10:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5239 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.033333 | 9.3723e-05 | 0.0013121 | 5239 | 174.6333
3083348 | Transient fault | 2024-04-19 22:52 | 2023 | 2024-04-19 22:53 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.016667 | 4.6862e-05 | 0.00065606 | 5690 | 94.8333
3128992 | Transient fault | 2024-11-16 19:21 | 2024 | 2024-11-16 19:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.033333 | 9.3723e-05 | 0.0013121 | 5760 | 192
3098895 | Feeder off on fault | 2024-06-21 17:17 | 2023 | 2024-06-21 19:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 107 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 1.7833 | 0.0050142 | 0.070199 | 5690 | 10147.1667
3157647 | MAGADI EX LANGATA | 2025-03-20 12:11 | 2024 | 2025-03-20 12:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.033333 | 9.3733e-05 | 0.0013123 | 5774 | 192.4667
2996754 | Transient fault | 2023-04-02 00:07 | 2022 | 2023-04-02 00:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.033333 | 9.3723e-05 | 0.0013121 | 5212 | 173.7333
3181599 | AY 2099 and AY 195 closing failure and weak betteris | 2025-07-04 03:06 | 2025 | 2025-07-04 06:38 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 212 | 2905.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 3.5333 | 0.010266 | 0.14373 | 12217 | 43166.7333
3083047 | Sustained fault | 2024-04-18 18:59 | 2023 | 2024-04-18 19:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 24 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.4 | 0.0011458 | 0.016042 | 12107 | 4842.8
2948374 | Feeder off on sustained fault | 2022-08-25 12:05 | 2022 | 2022-08-25 14:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 127 | 2865 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 2.1167 | 0.0060643 | 0.0849 | 11799 | 24974.55
2979932 | Transient fault | 2023-01-18 06:59 | 2022 | 2023-01-18 07:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.033333 | 9.5487e-05 | 0.0013368 | 11953 | 398.4333
2989325 | Transient fault | 2023-03-03 18:34 | 2022 | 2023-03-03 18:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.033333 | 9.5487e-05 | 0.0013368 | 11953 | 398.4333
3345837 | Transient fault | 2026-04-15 10:54 | 2025 | 2026-04-15 10:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2905.6 | 12807 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.066667 | 0.00019371 | 0.0027119 | 12807 | 853.8
3077666 | sustained fault | 2024-03-28 13:57 | 2023 | 2024-03-28 18:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 269 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 4.4833 | 0.012843 | 0.1798 | 12107 | 54279.7167
2984201 | Transient fault | 2023-02-08 15:35 | 2022 | 2023-02-08 15:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2865 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.033333 | 9.55e-05 | 0.001337 | 11953 | 398.4333
3077604 | A trip on Ngei ex Langata awaiting operator | 2024-03-28 13:57 | 2023 | 2024-03-28 14:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 36 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.6 | 0.0017188 | 0.024063 | 12107 | 7264.2
3014915 | Transient fault | 2023-06-19 07:50 | 2022 | 2023-06-19 07:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2864.6 | 12000 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.066667 | 0.00019097 | 0.0026736 | 12000 | 800
3102630 | Transient fault | 2024-07-11 09:10 | 2024 | 2024-07-11 09:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 31 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.51667 | 0.00148 | 0.020721 | 12107 | 6255.2833
3042132 | Feeder off on sustained fault | 2023-10-29 16:40 | 2023 | 2023-10-29 20:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 247 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 4.1167 | 0.011793 | 0.1651 | 12031 | 49527.6167
3020047 | Transient fault | 2023-07-17 08:49 | 2023 | 2023-07-17 08:53 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.066667 | 0.00019097 | 0.0026736 | 12031 | 802.0667
2938658 | Transient fault | 2022-07-11 08:54 | 2022 | 2022-07-11 09:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.33333 | 0.00095487 | 0.013368 | 11799 | 3933
3216268 | Transient fault | 2025-12-10 13:03 | 2025 | 2025-12-10 13:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 24 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.4 | 0.0011622 | 0.016271 | 12796 | 5118.4
3256933 | A Trip Ngei ex Langata awaiting operator , Ragati office informed | 2026-03-06 00:27 | 2025 | 2026-03-06 08:15 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 468 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 7.8 | 0.022664 | 0.31729 | 12796 | 99808.8
3223414 | controlled | 2025-12-31 23:54 | 2025 | 2026-01-01 00:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 41 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.68333 | 0.0019855 | 0.027797 | 12796 | 8743.9333
3228191 | Transient fault | 2026-01-10 15:42 | 2025 | 2026-01-10 15:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.05 | 0.00014528 | 0.0020339 | 12796 | 639.8
3228456 | Trip on faul | 2026-01-11 17:20 | 2025 | 2026-01-11 17:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 32 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.53333 | 0.0015497 | 0.021695 | 12796 | 6824.5333
3240589 | Sustained fault | 2026-02-09 14:15 | 2025 | 2026-02-09 17:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 222 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 3.7 | 0.010751 | 0.15051 | 12796 | 47345.2
3229539 | A trip on Ngei ex Langata awaiting operator not closing on scada | 2026-01-14 15:36 | 2025 | 2026-01-14 19:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 250 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 4.1667 | 0.012107 | 0.16949 | 12796 | 53316.6667
3190579 | Unestablished fault | 2025-08-17 11:00 | 2025 | 2025-08-17 13:29 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 149 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 2.4833 | 0.0072156 | 0.10102 | 12796 | 31776.7333
3210399 | sustained fault | 2025-11-14 14:34 | 2025 | 2025-11-14 15:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 36 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.6 | 0.0017434 | 0.024407 | 12796 | 7677.6
3126235 | Transient fault | 2024-11-05 12:59 | 2024 | 2024-11-05 13:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2864.6 | 12291 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.05 | 0.00014323 | 0.0020052 | 12291 | 614.55
3188503 | Sustained | 2025-08-10 14:21 | 2025 | 2025-08-10 16:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 109 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 1.8167 | 0.0052785 | 0.073899 | 12796 | 23246.0667
3174228 | TRANSIENT FAULT | 2025-05-26 19:07 | 2024 | 2025-05-26 19:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2905.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.033333 | 9.6853e-05 | 0.0013559 | 12217 | 407.2333
3188655 | Ngei ex Langata byd AY 2099 off awaiting operator, lunani informed. | 2025-08-11 08:11 | 2025 | 2025-08-11 12:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 281 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 4.6833 | 0.013608 | 0.19051 | 12796 | 59927.9333
2944048 | Transient fault | 2022-08-04 09:53 | 2022 | 2022-08-04 09:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.033333 | 9.5487e-05 | 0.0013368 | 11799 | 393.3
2980127 | Transient fault | 2023-01-18 20:24 | 2022 | 2023-01-18 20:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2865 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.05 | 0.00014325 | 0.0020055 | 11953 | 597.65
3001783 | Transient fault | 2023-04-18 17:31 | 2022 | 2023-04-18 17:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.15 | 0.00042969 | 0.0060157 | 11953 | 1792.95
3076488 | Transient fault | 2024-03-24 22:23 | 2023 | 2024-03-25 01:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 202 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 3.3667 | 0.0096442 | 0.13502 | 12107 | 40760.2333
3058188 | Transient fault | 2024-01-04 15:40 | 2023 | 2024-01-04 15:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.13333 | 0.00038195 | 0.0053473 | 12066 | 1608.8
3061242 | Transient fault | 2024-01-19 22:13 | 2023 | 2024-01-19 22:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.2 | 0.00057292 | 0.0080209 | 12066 | 2413.2
2953091 | Open point Y5297 closed by third party | 2022-09-16 11:29 | 2022 | 2022-09-16 14:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 181 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 3.0167 | 0.0086415 | 0.12098 | 11799 | 35593.65
3166210 | Transient fault | 2025-04-21 21:19 | 2024 | 2025-04-21 21:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2864.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.066667 | 0.00019097 | 0.0026736 | 12217 | 814.4667
3043302 | Transient fault | 2023-11-02 15:03 | 2023 | 2023-11-02 15:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.1 | 0.00028646 | 0.0040104 | 12031 | 1203.1
2971423 | Sustained fault | 2022-12-05 23:13 | 2022 | 2022-12-05 23:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 23 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.38333 | 0.0010981 | 0.015373 | 11953 | 4581.9833
3044310 | Single phasing on Ngei ex Langata | 2023-11-06 19:25 | 2023 | 2023-11-06 21:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 130 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 2.1667 | 0.0062066 | 0.086893 | 12066 | 26143
3086478 | Transient fault | 2024-04-30 11:23 | 2023 | 2024-04-30 11:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.033333 | 9.5487e-05 | 0.0013368 | 12107 | 403.5667
3076550 | Sustained fault | 2024-03-25 01:46 | 2023 | 2024-03-25 11:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 610 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 10.1667 | 0.029123 | 0.40773 | 12107 | 123087.8333
3075015 | Transient fault | 2024-03-18 18:09 | 2023 | 2024-03-18 18:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.2 | 0.00057292 | 0.0080209 | 12107 | 2421.4
3102801 | Transient fault | 2024-07-11 18:48 | 2024 | 2024-07-11 19:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 53 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.88333 | 0.0025304 | 0.035426 | 12107 | 10694.5167
2938785 | Trip on fault | 2022-07-11 19:40 | 2022 | 2022-07-12 07:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 720 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 12 | 0.034375 | 0.48125 | 11799 | 141588
2992105 | Transient fault | 2023-03-16 04:33 | 2022 | 2023-03-16 04:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.23333 | 0.00066841 | 0.0093577 | 11953 | 2789.0333
3048215 | Transient fault | 2023-11-20 18:16 | 2023 | 2023-11-20 19:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 76 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 1.2667 | 0.0036285 | 0.050799 | 12066 | 15283.6
3285754 | Transient fault | 2026-03-20 19:25 | 2025 | 2026-03-20 19:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2905.6 | 12860 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.083333 | 0.00024213 | 0.0033899 | 12860 | 1071.6667
2967715 | Transient fault | 2022-11-20 13:18 | 2022 | 2022-11-20 13:29 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 0.18333 | 0.00052518 | 0.0073525 | 11953 | 2191.3833
3216428 | Trip on fault | 2025-12-11 07:51 | 2025 | 2025-12-11 09:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 100 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 1.6667 | 0.0048427 | 0.067797 | 12796 | 21326.6667
2955076 | NGEI EX LANGATA | 2022-09-25 15:17 | 2022 | 2022-09-25 15:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2865 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.083333 | 0.00023875 | 0.0033425 | 11799 | 983.25
2956846 | Transient fault | 2022-10-03 17:10 | 2022 | 2022-10-03 17:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2865 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.016667 | 4.775e-05 | 0.0006685 | 11799 | 196.65
3140604 | transient | 2025-01-09 16:02 | 2024 | 2025-01-09 16:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.11667 | 0.0003342 | 0.0046788 | 12297 | 1434.65
2936578 | TRANSIENT | 2022-07-01 03:38 | 2022 | 2022-07-01 03:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.15 | 0.00042969 | 0.0060157 | 11799 | 1769.85
3112800 | Transient fault | 2024-09-04 11:54 | 2024 | 2024-09-04 12:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.1 | 0.00019549 | 0.0027369 | 837 | 83.7
3004825 | Transient fault | 2023-05-01 06:49 | 2022 | 2023-05-01 06:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 0.016667 | 3.2582e-05 | 0.00045614 | 730 | 12.1667
2989602 | Transient fault | 2023-03-05 16:32 | 2022 | 2023-03-05 16:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.016667 | 3.2582e-05 | 0.00045614 | 724 | 12.0667
3154384 | Sustained fault | 2025-03-09 15:40 | 2024 | 2025-03-09 16:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.8 | 0.0015639 | 0.021895 | 933 | 746.4
3076211 | Transient fault | 2024-03-23 21:49 | 2023 | 2024-03-23 21:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.033333 | 6.5163e-05 | 0.00091229 | 837 | 27.9
2988745 | Transient fault | 2023-03-01 10:05 | 2022 | 2023-03-01 10:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.05 | 9.7745e-05 | 0.0013684 | 724 | 36.2
3021598 | Transient fault | 2023-07-25 15:29 | 2023 | 2023-07-25 15:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.033333 | 6.5163e-05 | 0.00091229 | 763 | 25.4333
3173696 | Transient fault | 2025-05-24 09:15 | 2024 | 2025-05-24 09:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.11667 | 0.00022807 | 0.003193 | 933 | 108.85
3033114 | Feeder off on fault. Awaiting operator | 2023-09-20 13:58 | 2023 | 2023-09-20 14:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.28333 | 0.00055389 | 0.0077544 | 763 | 216.1833
2955390 | Transient fault | 2022-09-26 16:01 | 2022 | 2022-09-26 16:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 698 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.05 | 9.7745e-05 | 0.0013684 | 698 | 34.9
3116306 | Transient fault | 2024-09-22 07:33 | 2024 | 2024-09-22 07:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.016667 | 3.2582e-05 | 0.00045614 | 837 | 13.95
2937712 | Transient fault | 2022-07-06 14:20 | 2022 | 2022-07-06 14:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 1954.9 | 698 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.11667 | 0.00022807 | 0.003193 | 698 | 81.4333
3252699 | Transient fault | 2026-02-28 09:39 | 2025 | 2026-02-28 09:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 15 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.25 | 0.00048872 | 0.0068421 | 988 | 247
3215287 | A trip on Ndalati ex Langata | 2025-12-05 16:36 | 2025 | 2025-12-05 20:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 213 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 3.55 | 0.0069399 | 0.097159 | 988 | 3507.4
3264462 | Trip on fault | 2026-03-14 01:51 | 2025 | 2026-03-14 02:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 1954.9 | 1008 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.18333 | 0.0003584 | 0.0050176 | 1008 | 184.8
3244062 | Transient fault | 2026-02-09 16:26 | 2025 | 2026-02-09 16:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.016667 | 3.2582e-05 | 0.00045614 | 988 | 16.4667
3091013 | Transient fault | 2024-05-16 19:30 | 2023 | 2024-05-16 19:31 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.016667 | 3.2582e-05 | 0.00045614 | 837 | 13.95
3117630 | Transient fault | 2024-09-27 20:37 | 2024 | 2024-09-27 20:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 89 | 1954.9 | 924 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 1.4833 | 0.0028998 | 0.040597 | 924 | 1370.6
3013116 | Transient fault | 2023-06-10 15:00 | 2022 | 2023-06-10 15:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.16667 | 0.00032582 | 0.0045614 | 730 | 121.6667
3062878 | Transient fault | 2024-01-28 08:30 | 2023 | 2024-01-28 08:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.033333 | 6.5163e-05 | 0.00091229 | 796 | 26.5333
2999327 | Transient fault | 2023-04-09 18:54 | 2022 | 2023-04-09 18:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.083333 | 0.00016291 | 0.0022807 | 724 | 60.3333
2938390 | Sustained fault on Ndalat ex Langata | 2022-07-09 12:00 | 2022 | 2022-07-09 14:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 122 | 1954.9 | 698 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 2.0333 | 0.003975 | 0.055649 | 698 | 1419.2667
3057792 | Transient fault | 2024-01-02 22:14 | 2023 | 2024-01-02 22:27 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.21667 | 0.00042356 | 0.0059299 | 796 | 172.4667
2993750 | TRANSIENT FAULT | 2023-03-23 07:01 | 2022 | 2023-03-23 07:05 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.066667 | 0.00013033 | 0.0018246 | 724 | 48.2667
3006623 | Transient fault. | 2023-05-09 09:07 | 2022 | 2023-05-09 09:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 26 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 0.43333 | 0.00084712 | 0.01186 | 730 | 316.3333
3001999 | A trip on Ndalat ex Langata awaiting operator not closing on scada | 2023-04-19 15:23 | 2022 | 2023-04-19 16:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 70 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 1.1667 | 0.0022807 | 0.03193 | 730 | 851.6667
3012785 | Ndalat ex Langata sustained | 2023-06-09 04:39 | 2022 | 2023-06-09 14:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 591 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 9.85 | 0.019256 | 0.26958 | 730 | 7190.5
2942161 | Unestablished fault | 2022-07-27 09:08 | 2022 | 2022-07-27 11:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 140 | 1954.9 | 698 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 2.3333 | 0.0045614 | 0.06386 | 698 | 1628.6667
3072249 | Transient fault | 2024-03-07 10:36 | 2023 | 2024-03-07 10:38 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.033333 | 6.5163e-05 | 0.00091229 | 837 | 27.9
3054811 | Transient fault | 2023-12-18 13:05 | 2023 | 2023-12-18 13:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.083333 | 0.00016291 | 0.0022807 | 796 | 66.3333
3012665 | Transient fault | 2023-06-08 10:35 | 2022 | 2023-06-08 10:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.083333 | 0.00016291 | 0.0022807 | 730 | 60.8333
3117619 | A trip on Ndalat ex Langata.Nyameya informed. | 2024-09-27 19:01 | 2024 | 2024-09-27 20:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 1954.9 | 924 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 1.6 | 0.0031278 | 0.04379 | 924 | 1478.4
3089453 | sustained fault | 2024-05-10 07:23 | 2023 | 2024-05-10 13:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 395 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 6.5833 | 0.01287 | 0.18018 | 837 | 5510.25
3114750 | Trip on fault | 2024-09-14 12:11 | 2024 | 2024-09-14 12:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 15 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.25 | 0.00048872 | 0.0068421 | 837 | 209.25
3130406 | Transient fault | 2024-11-22 18:18 | 2024 | 2024-11-22 18:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0 | 0 | 0 | 925 | 0
3086233 | Sustained fault | 2024-04-29 17:56 | 2023 | 2024-04-29 21:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 186 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 3.1 | 0.0060602 | 0.084843 | 837 | 2594.7
3022661 | Transient fault | 2023-07-31 15:15 | 2023 | 2023-07-31 15:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.05 | 9.7745e-05 | 0.0013684 | 763 | 38.15
3145974 | Transient fault | 2025-01-31 11:24 | 2024 | 2025-01-31 12:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 61 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 1.0167 | 0.0019875 | 0.027825 | 925 | 940.4167
3056390 | Transient fault | 2023-12-26 19:11 | 2023 | 2023-12-26 19:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 6.5163e-05 | 0.00091229 | 796 | 26.5333
3148226 | Transient fault | 2025-02-11 12:06 | 2024 | 2025-02-11 12:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.066667 | 0.00013033 | 0.0018246 | 925 | 61.6667
3141928 | Transient fault | 2025-01-15 20:24 | 2024 | 2025-01-15 20:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.033333 | 6.5163e-05 | 0.00091229 | 925 | 30.8333
3085161 | Broken jumper at AY 66 | 2024-04-25 14:09 | 2023 | 2024-04-25 14:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.05 | 9.7745e-05 | 0.0013684 | 837 | 41.85
3084911 | TRANSIENT FAULT | 2024-04-25 01:19 | 2023 | 2024-04-25 03:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 125 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 2.0833 | 0.0040727 | 0.057018 | 837 | 1743.75
2986182 | Transient fault | 2023-02-17 19:19 | 2022 | 2023-02-17 19:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.05 | 9.7745e-05 | 0.0013684 | 724 | 36.2
3056278 | Transient fault | 2023-12-26 11:14 | 2023 | 2023-12-26 11:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.066667 | 0.00013033 | 0.0018246 | 796 | 53.0667
3130580 | Transient fault | 2024-11-23 19:30 | 2024 | 2024-11-23 19:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.1 | 0.00019549 | 0.0027369 | 925 | 92.5
3185766 | transient fault | 2025-07-28 07:40 | 2025 | 2025-07-28 07:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.033333 | 6.5163e-05 | 0.00091229 | 988 | 32.9333
3260588 | sustained fault | 2026-03-10 18:11 | 2025 | 2026-03-10 21:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 170 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 2.8333 | 0.0055389 | 0.077544 | 988 | 2799.3333
3077328 | Transient Fault | 2024-03-27 15:41 | 2023 | 2024-03-27 15:42 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.016667 | 3.2582e-05 | 0.00045614 | 837 | 13.95
3035228 | A trip on Ndalati ex Langata | 2023-09-28 06:30 | 2023 | 2023-09-28 06:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 25 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.41667 | 0.00081454 | 0.011404 | 763 | 317.9167
3007600 | Unestablished fault | 2023-05-14 01:45 | 2022 | 2023-05-14 03:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 85 | 1954.9 | 730 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 1.4167 | 0.0027694 | 0.038772 | 730 | 1034.1667
2960703 | Transient fault | 2022-10-21 11:56 | 2022 | 2022-10-21 13:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 1.1167 | 0.002183 | 0.030562 | 724 | 808.4667
3044285 | Transient fault | 2023-11-06 17:36 | 2023 | 2023-11-06 17:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.05 | 9.7745e-05 | 0.0013684 | 796 | 39.8
3114941 | Trip on fault | 2024-09-15 20:27 | 2024 | 2024-09-15 20:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.11667 | 0.00022807 | 0.003193 | 837 | 97.65
2992871 | Ndalat ex Langata off awaiting operator not closing on SCADA | 2023-03-19 21:17 | 2022 | 2023-03-19 22:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 71 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 1.1833 | 0.0023133 | 0.032386 | 724 | 856.7333
3078635 | Transient fault | 2024-04-02 13:48 | 2023 | 2024-04-02 13:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.033333 | 6.5163e-05 | 0.00091229 | 837 | 27.9
2984897 | A trip on Ndalat ex Langata - awaiting operator | 2023-02-12 17:04 | 2022 | 2023-02-12 18:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 1.1167 | 0.002183 | 0.030562 | 724 | 808.4667
3053481 | Transient fault | 2023-12-12 10:06 | 2023 | 2023-12-12 10:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 6.5163e-05 | 0.00091229 | 796 | 26.5333
3135101 | Trip on fault awaiting operator | 2024-12-12 09:47 | 2024 | 2024-12-12 10:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.8 | 0.0029839 | 0.041775 | 32702 | 26161.6
2981127 | Transient fault | 2023-01-24 06:48 | 2022 | 2023-01-24 06:50 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.016667 | 6.2165e-05 | 0.00087031 | 33290 | 554.8333
3114981 | Transient fault | 2024-09-16 10:11 | 2024 | 2024-09-16 10:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
3144485 | transient | 2025-01-27 00:02 | 2024 | 2025-01-27 00:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.11667 | 0.00043516 | 0.0060922 | 32702 | 3815.2333
3058625 | Transient fault | 2024-01-06 19:59 | 2023 | 2024-01-06 19:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0 | 0 | 0 | 33331 | 0
3053463 | Transient fault | 2023-12-12 08:56 | 2023 | 2023-12-12 09:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.11667 | 0.00043516 | 0.0060922 | 33331 | 3888.6167
3105191 | Transient fault | 2024-07-24 20:00 | 2024 | 2024-07-24 20:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.16667 | 0.00062165 | 0.0087031 | 33325 | 5554.1667
2944833 | Transient fault | 2022-08-08 10:16 | 2022 | 2022-08-08 10:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.033333 | 0.00012433 | 0.0017406 | 32658 | 1088.6
3018424 | Transient fault | 2023-07-07 19:50 | 2023 | 2023-07-07 19:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33295 | 1109.8333
2953664 | Transient fault | 2022-09-19 10:57 | 2022 | 2022-09-19 11:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.083333 | 0.00031082 | 0.0043516 | 32658 | 2721.5
2946493 | Transient fault | 2022-08-16 17:42 | 2022 | 2022-08-16 18:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.85 | 0.0031704 | 0.044386 | 32658 | 27759.3
2971332 | Soweto ex Langata Trip on fault awaiting operator | 2022-12-05 14:30 | 2022 | 2022-12-05 16:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 115 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 1.9167 | 0.007149 | 0.10009 | 33290 | 63805.8333
2975322 | Sustained fault on Soweto ex Langata byd AY5050 | 2022-12-25 15:05 | 2022 | 2022-12-25 16:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 103 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 1.7167 | 0.006403 | 0.089642 | 33290 | 57147.8333
3166112 | Transient fault | 2025-04-21 13:57 | 2024 | 2025-04-21 14:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.05 | 0.0001865 | 0.0026109 | 31280 | 1564
2990612 | Transient fault | 2023-03-09 14:16 | 2022 | 2023-03-09 14:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.066667 | 0.00024866 | 0.0034812 | 33290 | 2219.3333
3153314 | Overload | 2025-03-04 19:29 | 2024 | 2025-03-05 07:03 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 694 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 11.5667 | 0.043143 | 0.604 | 31280 | 361805.3333
3119347 | Transient fault | 2024-10-04 13:34 | 2024 | 2024-10-04 13:38 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 0.066667 | 0.00024866 | 0.0034812 | 32679 | 2178.6
3156125 | Transient fault | 2025-03-14 10:44 | 2024 | 2025-03-14 10:47 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.05 | 0.0001865 | 0.0026109 | 31280 | 1564
3297862 | Transient Fault | 2026-03-29 20:56 | 2025 | 2026-03-29 21:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.066667 | 0.00024866 | 0.0034812 | 27892 | 1859.4667
3366623 | A Trip on Soweto ex Langata not closing on scada station unmanned Miriti inform | 2026-04-29 21:05 | 2025 | 2026-04-29 21:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 41 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.68333 | 0.0025488 | 0.035683 | 26342 | 18000.3667
3285689 | Transient fault | 2026-03-20 15:11 | 2025 | 2026-03-20 15:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.11667 | 0.00043516 | 0.0060922 | 27892 | 3254.0667
3285705 | Transient fault | 2026-03-20 15:18 | 2025 | 2026-03-20 15:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.05 | 0.0001865 | 0.0026109 | 27892 | 1394.6
3286470 | Transient fault | 2026-03-21 15:39 | 2025 | 2026-03-21 15:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.016667 | 6.2165e-05 | 0.00087031 | 27892 | 464.8667
3364638 | Transient Fault | 2026-04-28 16:45 | 2025 | 2026-04-28 17:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 35 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.58333 | 0.0021758 | 0.030461 | 26342 | 15366.1667
3356696 | Transient fault | 2026-04-23 11:55 | 2025 | 2026-04-23 12:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.1 | 0.00037299 | 0.0052219 | 26342 | 2634.2
3032475 | Transient fault | 2023-09-18 07:31 | 2023 | 2023-09-18 07:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.05 | 0.0001865 | 0.0026109 | 33295 | 1664.75
3032482 | sustained | 2023-09-18 07:31 | 2023 | 2023-09-18 10:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 198 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 3.3 | 0.012309 | 0.17232 | 33295 | 109873.5
3086653 | Sustained fault | 2024-05-01 05:27 | 2023 | 2024-05-01 09:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 250 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 4.1667 | 0.015541 | 0.21758 | 33325 | 138854.1667
3009577 | Feeder off on sustained fault | 2023-05-23 17:06 | 2022 | 2023-05-23 17:48 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 42 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 0.7 | 0.0026109 | 0.036553 | 33284 | 23298.8
3014002 | Transient fault | 2023-06-14 15:59 | 2022 | 2023-06-14 16:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 23 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.38333 | 0.0014298 | 0.020017 | 33284 | 12758.8667
2959960 | Soweto ex Langata Trip on fault awaiting operator | 2022-10-18 08:30 | 2022 | 2022-10-18 08:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.15 | 0.00055948 | 0.0078328 | 33290 | 4993.5
2968321 | A trip on Soweto ex Langata, awaiting operator | 2022-11-22 14:00 | 2022 | 2022-11-22 17:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 217 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 3.6167 | 0.01349 | 0.18886 | 33290 | 120398.8333
3122237 | TRANSIENT FAULT | 2024-10-18 02:17 | 2024 | 2024-10-18 02:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 0.066667 | 0.00024866 | 0.0034812 | 32679 | 2178.6
3046092 | Transient fault | 2023-11-13 02:49 | 2023 | 2023-11-13 02:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.083333 | 0.00031082 | 0.0043516 | 33331 | 2777.5833
3153120 | Transient fault | 2025-03-03 15:48 | 2024 | 2025-03-03 16:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.23333 | 0.00087031 | 0.012184 | 31280 | 7298.6667
3011112 | Transient fault | 2023-05-30 15:37 | 2022 | 2023-05-30 15:39 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33284 | 1109.4667
2956291 | Transient fault | 2022-10-01 06:53 | 2022 | 2022-10-01 07:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 15 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.25 | 0.00093247 | 0.013055 | 32658 | 8164.5
2964952 | Transient fault | 2022-11-08 19:19 | 2022 | 2022-11-08 19:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
3255992 | Transient fault | 2026-03-04 17:10 | 2025 | 2026-03-04 17:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 35 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.58333 | 0.0021758 | 0.030461 | 27872 | 16258.6667
3207346 | Transient fault | 2025-11-02 08:44 | 2025 | 2025-11-02 08:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.083333 | 0.00031082 | 0.0043516 | 27872 | 2322.6667
3207401 | TRANSIENT FAULT | 2025-11-02 11:01 | 2025 | 2025-11-02 11:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.18333 | 0.00068382 | 0.0095734 | 27872 | 5109.8667
3221420 | A trip on Soweto ex Langata awaiting operator (Vacant shift) | 2025-12-25 21:33 | 2025 | 2025-12-25 23:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 120 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 2 | 0.0074598 | 0.10444 | 27872 | 55744
3217170 | Transient Fault | 2025-12-14 03:48 | 2025 | 2025-12-14 03:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.066667 | 0.00024866 | 0.0034812 | 27872 | 1858.1333
3261518 | Transient fault | 2026-03-11 15:58 | 2025 | 2026-03-11 16:15 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.28333 | 0.0010568 | 0.014795 | 27872 | 7897.0667
3257627 | Transient fault - Not closing on SCADA | 2026-03-06 17:26 | 2025 | 2026-03-06 18:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 38 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.63333 | 0.0023623 | 0.033072 | 27872 | 17652.2667
3222599 | Transient fault | 2025-12-29 18:03 | 2025 | 2025-12-29 18:49 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 46 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.76667 | 0.0028596 | 0.040034 | 27872 | 21368.5333
3258963 | Transient fault | 2026-03-08 09:56 | 2025 | 2026-03-08 09:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.016667 | 6.2165e-05 | 0.00087031 | 27872 | 464.5333
3222891 | A trip on Soweto ex Langata | 2025-12-30 13:51 | 2025 | 2025-12-30 15:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 86 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 1.4333 | 0.0053462 | 0.074847 | 27872 | 39949.8667
3237779 | Transient fault | 2026-02-04 12:51 | 2025 | 2026-02-04 14:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 93 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.55 | 0.0057813 | 0.080939 | 27872 | 43201.6
3210574 | Trip on fault | 2025-11-15 08:00 | 2025 | 2025-11-16 11:29 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1649 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 27.4833 | 0.10251 | 1.4351 | 27872 | 766015.4667
3131204 | Transient fault | 2024-11-26 10:13 | 2024 | 2024-11-26 10:21 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.13333 | 0.00049732 | 0.0069625 | 32702 | 4360.2667
3086287 | Transient fault | 2024-04-29 22:52 | 2023 | 2024-04-29 22:54 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
3057584 | Transient fault | 2024-01-02 01:53 | 2023 | 2024-01-02 06:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 281 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 4.6833 | 0.017468 | 0.24456 | 33331 | 156100.1833
3046065 | Transient fault | 2023-11-12 19:26 | 2023 | 2023-11-12 19:33 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.11667 | 0.00043516 | 0.0060922 | 33331 | 3888.6167
2991139 | Transient fault | 2023-03-12 09:09 | 2022 | 2023-03-12 09:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | -129 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | -2.15 | -0.0080193 | -0.11227 | 33290 | -71573.5
3000946 | Transient fault | 2023-04-15 08:33 | 2022 | 2023-04-15 08:36 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
3060479 | Transient fault | 2024-01-17 00:23 | 2023 | 2024-01-17 00:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.05 | 0.0001865 | 0.0026109 | 33331 | 1666.55
3165536 | Unestablished fault | 2025-04-19 10:35 | 2024 | 2025-04-19 12:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 1.6 | 0.0059678 | 0.08355 | 31280 | 50048
2952230 | Transient fault | 2022-09-12 12:02 | 2022 | 2022-09-12 12:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.2 | 0.00074598 | 0.010444 | 32658 | 6531.6
2999585 | Transient fault | 2023-04-11 02:48 | 2022 | 2023-04-11 02:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.066667 | 0.00024866 | 0.0034812 | 33290 | 2219.3333
3002166 | Transient fault. | 2023-04-20 09:56 | 2022 | 2023-04-20 09:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33284 | 1109.4667
3014110 | Transient fault | 2023-06-15 09:23 | 2022 | 2023-06-15 09:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33284 | 1109.4667
3116315 | Transient fault | 2024-09-22 12:59 | 2024 | 2024-09-22 13:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.16667 | 0.00062165 | 0.0087031 | 33325 | 5554.1667
3152897 | Delayed outage on;N/south 1 ex Juja,N/south 2 ex Umoja,Part of South 2 ex Embaka | 2025-03-02 19:10 | 2024 | 2025-03-02 19:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.05 | 0.0001865 | 0.0026109 | 31280 | 1564
3152907 | overload | 2025-03-02 19:16 | 2024 | 2025-03-02 22:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 168 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.8 | 0.010444 | 0.14621 | 31280 | 87584
3046852 | Unestablished fault. | 2023-11-15 16:46 | 2023 | 2023-11-15 19:01 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 135 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 2.25 | 0.0083923 | 0.11749 | 33331 | 74994.75
3108700 | Transient fault | 2024-08-14 08:20 | 2024 | 2024-08-14 08:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 0.16667 | 0.00062165 | 0.0087031 | 33325 | 5554.1667
3101623 | Transient fault | 2024-07-06 17:50 | 2024 | 2024-07-06 17:52 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
3053013 | Feeder off on sustained fault | 2023-12-09 23:33 | 2023 | 2023-12-10 14:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 922 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 15.3667 | 0.057316 | 0.80243 | 33331 | 512186.3667
3148889 | Soweto ex Langata sustained with broken jumper at cable take off, Waweru informe | 2025-02-13 20:00 | 2024 | 2025-02-13 23:37 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 217 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 3.6167 | 0.01349 | 0.18886 | 32702 | 118272.2333
2940308 | Transient fault | 2022-07-18 19:09 | 2022 | 2022-07-18 19:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.05 | 0.0001865 | 0.0026109 | 32658 | 1632.9
3031830 | Soweto ex Langata Off awaiting operator iNFORMED eVANS sIRIBA | 2023-09-14 10:01 | 2023 | 2023-09-14 10:32 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 31 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.51667 | 0.0019271 | 0.02698 | 33295 | 17202.4167
3119478 | Transient fault | 2024-10-05 13:20 | 2024 | 2024-10-05 13:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 0.033333 | 0.00012433 | 0.0017406 | 32679 | 1089.3
3085390 | Transient fault | 2024-04-26 11:50 | 2023 | 2024-04-26 12:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.23333 | 0.00087031 | 0.012184 | 33325 | 7775.8333
2958576 | Transient fault | 2022-10-11 10:04 | 2022 | 2022-10-11 10:07 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
3188599 | Sustained fault on Soweto ex Langata-AY 5300. Ragati office informed. | 2025-08-11 01:09 | 2025 | 2025-08-11 14:34 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 805 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 13.4167 | 0.050043 | 0.7006 | 27872 | 373949.3333
3059850 | Transient fault | 2024-01-13 11:36 | 2023 | 2024-01-13 11:42 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.1 | 0.00037299 | 0.0052219 | 33331 | 3333.1
3109489 | Soweto ex Langata off awaiting operator.Informed Ragati emergency. | 2024-08-18 09:01 | 2024 | 2024-08-18 14:44 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 343 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 5.7167 | 0.021323 | 0.29852 | 33325 | 190507.9167
2949741 | Transient fault | 2022-08-31 19:58 | 2022 | 2022-08-31 19:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.016667 | 6.2165e-05 | 0.00087031 | 32658 | 544.3
3166151 | Transien fault | 2025-04-21 18:10 | 2024 | 2025-04-21 18:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0 | 0 | 0 | 31280 | 0
3144807 | Transient fault | 2025-01-27 17:49 | 2024 | 2025-01-27 18:15 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 26 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.43333 | 0.0016163 | 0.022628 | 32702 | 14170.8667
2973633 | Soweto ex Langata off awaiting opwerator | 2022-12-16 04:19 | 2022 | 2022-12-16 07:35 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 196 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 3.2667 | 0.012184 | 0.17058 | 33290 | 108747.3333
2973413 | Soweto ex Langata off awaiting operator | 2022-12-15 00:40 | 2022 | 2022-12-15 05:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 306 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 5.1 | 0.019022 | 0.26631 | 33290 | 169779
3026145 | Transient fault | 2023-08-18 19:09 | 2023 | 2023-08-18 19:11 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33295 | 1109.8333
3086477 | Transient fault | 2024-04-30 11:25 | 2023 | 2024-04-30 11:56 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 31 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.51667 | 0.0019271 | 0.02698 | 33325 | 17217.9167
3166808 | transient fault | 2025-04-23 20:14 | 2024 | 2025-04-23 20:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.15 | 0.00055948 | 0.0078328 | 31280 | 4692
3165413 | Transient fault | 2025-04-18 14:36 | 2024 | 2025-04-18 14:38 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.033333 | 0.00012433 | 0.0017406 | 31280 | 1042.6667
2975549 | Feeder off on sustained fault | 2022-12-27 07:29 | 2022 | 2022-12-27 15:26 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 477 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 7.95 | 0.029653 | 0.41514 | 33290 | 264655.5
3155844 | transient | 2025-03-13 11:20 | 2024 | 2025-03-13 11:23 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.05 | 0.0001865 | 0.0026109 | 31280 | 1564
3091566 | Transient fault | 2024-05-19 22:22 | 2023 | 2024-05-19 22:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.1 | 0.00037299 | 0.0052219 | 33325 | 3332.5
2974579 | Transient fault | 2022-12-21 06:40 | 2022 | 2022-12-21 06:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
3029285 | Transient fault | 2023-09-04 12:17 | 2023 | 2023-09-04 12:20 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.05 | 0.0001865 | 0.0026109 | 33295 | 1664.75
2950184 | TRANSIENT FAULT | 2022-09-02 20:10 | 2022 | 2022-09-02 20:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.033333 | 0.00012433 | 0.0017406 | 32658 | 1088.6
2980322 | Transient fault | 2023-01-19 19:36 | 2022 | 2023-01-19 19:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 0.16667 | 0.00062165 | 0.0087031 | 33290 | 5548.3333
3050660 | Transient fault | 2023-11-29 11:15 | 2023 | 2023-11-29 11:57 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 42 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 0.7 | 0.0026109 | 0.036553 | 33331 | 23331.7
3127713 | Transient fault | 2024-11-11 15:43 | 2024 | 2024-11-11 15:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.033333 | 0.00012433 | 0.0017406 | 32702 | 1090.0667
3107235 | Transient fault | 2024-08-05 19:38 | 2024 | 2024-08-05 19:51 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 0.21667 | 0.00080815 | 0.011314 | 33325 | 7220.4167
3140587 | Transient fault | 2025-01-09 11:12 | 2024 | 2025-01-09 11:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.033333 | 0.00012433 | 0.0017406 | 32702 | 1090.0667
3122236 | sustained fault | 2024-10-18 02:57 | 2024 | 2024-10-18 08:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 315 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 5.25 | 0.019582 | 0.27415 | 32679 | 171564.75
3145408 | Soweto ex Langata off awaiting operator | 2025-01-29 23:51 | 2024 | 2025-01-30 02:28 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 157 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 2.6167 | 0.0097599 | 0.13664 | 32702 | 85570.2333
3106037 | Transient fault | 2024-07-29 20:11 | 2024 | 2024-07-29 20:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.05 | 0.0001865 | 0.0026109 | 33325 | 1666.25
3136747 | Trip on fault | 2024-12-19 20:30 | 2024 | 2024-12-19 21:07 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 37 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.61667 | 0.0023001 | 0.032201 | 32702 | 20166.2333
3102940 | Transient fault | 2024-07-12 18:14 | 2024 | 2024-07-12 18:17 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.05 | 0.0001865 | 0.0026109 | 33325 | 1666.25
2995167 | Transient fault | 2023-03-27 20:25 | 2022 | 2023-03-27 20:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.083333 | 0.00031082 | 0.0043516 | 33290 | 2774.1667
3167526 | Transient fault | 2025-04-26 19:13 | 2024 | 2025-04-26 19:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.05 | 0.0001865 | 0.0026109 | 31280 | 1564
3077479 | Single phasing on Soweto ex Langata Mageto informed | 2024-03-28 07:45 | 2023 | 2024-03-28 11:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 253 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 4.2167 | 0.015728 | 0.22019 | 33325 | 140520.4167
3055644 | Transient fault | 2023-12-22 06:42 | 2023 | 2023-12-22 06:45 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.05 | 0.0001865 | 0.0026109 | 33331 | 1666.55
3000062 | Transient fault | 2023-04-12 10:27 | 2022 | 2023-04-12 10:30 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
2989145 | Transient fault | 2023-03-02 20:32 | 2022 | 2023-03-02 21:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 37 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 0.61667 | 0.0023001 | 0.032201 | 33290 | 20528.8333
3152519 | Transient fault | 2025-02-28 19:12 | 2024 | 2025-02-28 19:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.21667 | 0.00080815 | 0.011314 | 31280 | 6777.3333
3152536 | sustained fault | 2025-02-28 20:00 | 2024 | 2025-03-01 01:22 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | UNESTABLISHED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 322 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 5.3667 | 0.020017 | 0.28024 | 31280 | 167869.3333
3039886 | Transient fault | 2023-10-18 19:05 | 2023 | 2023-10-18 19:06 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.016667 | 6.2165e-05 | 0.00087031 | 33295 | 554.9167
3106195 | Transient fault | 2024-07-30 14:07 | 2024 | 2024-07-30 14:09 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
3052929 | Transient fault | 2023-12-09 12:38 | 2023 | 2023-12-09 12:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33331 | 1111.0333
3148734 | Transient fault | 2025-02-13 08:13 | 2024 | 2025-02-13 08:14 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.016667 | 6.2165e-05 | 0.00087031 | 32702 | 545.0333
3138555 | Transient fault | 2024-12-28 20:45 | 2024 | 2024-12-28 20:46 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 0.016667 | 6.2165e-05 | 0.00087031 | 32702 | 545.0333
3243915 | A Trip on Soweto ex Langata awaiting operator not closuing on scada (Vacant shi | 2026-02-15 12:55 | 2025 | 2026-02-15 13:40 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 45 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.75 | 0.0027974 | 0.039164 | 27872 | 20904
3229345 | TRANSIENT FAULT | 2026-01-14 07:56 | 2025 | 2026-01-14 07:58 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.033333 | 0.00012433 | 0.0017406 | 27872 | 929.0667
3229348 | TRANSIENT FAULT | 2026-01-14 08:08 | 2025 | 2026-01-14 08:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.033333 | 0.00012433 | 0.0017406 | 27872 | 929.0667
3230054 | A trip on Soweto ex Langata awaiting operator not closing on scada | 2026-01-15 22:19 | 2025 | 2026-01-15 23:41 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 82 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 1.3667 | 0.0050975 | 0.071365 | 27872 | 38091.7333
3243459 | A Trip on Soweto ex Langata awaiting operator not closuing on scada (Vacant shi | 2026-02-14 15:31 | 2025 | 2026-02-14 16:08 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 37 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.61667 | 0.0023001 | 0.032201 | 27872 | 17187.7333
3017574 | Transient fault. | 2023-07-03 21:20 | 2023 | 2023-07-03 21:24 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.066667 | 0.00024866 | 0.0034812 | 33295 | 2219.6667
2975388 | Transient fault | 2022-12-26 08:22 | 2022 | 2022-12-26 08:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.05 | 0.0001865 | 0.0026109 | 33290 | 1664.5
3022896 | Feeder off on sustained fault | 2023-08-01 14:24 | 2023 | 2023-08-01 17:12 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 168 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 2.8 | 0.010444 | 0.14621 | 33295 | 93226
2951812 | Transient fault | 2022-09-09 21:16 | 2022 | 2022-09-09 21:19 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.05 | 0.0001865 | 0.0026109 | 32658 | 1632.9
3104154 | Transient | 2024-07-18 19:41 | 2024 | 2024-07-18 19:43 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
2943454 | Transient fault | 2022-08-01 20:00 | 2022 | 2022-08-01 20:04 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.066667 | 0.00024866 | 0.0034812 | 32658 | 2177.2
2973125 | Transient fault | 2022-12-14 00:04 | 2022 | 2022-12-14 00:16 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.2 | 0.00074598 | 0.010444 | 33290 | 6658
2975362 | Transient fault | 2022-12-25 19:25 | 2022 | 2022-12-25 20:02 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 37 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.61667 | 0.0023001 | 0.032201 | 33290 | 20528.8333
3127174 | Transient fault | 2024-11-09 06:08 | 2024 | 2024-11-09 06:10 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.033333 | 0.00012433 | 0.0017406 | 32702 | 1090.0667
3093823 | Sustained fault on Soweto ex Langata byd AY 5300, Siriba informed. | 2024-05-28 14:25 | 2023 | 2024-05-28 18:59 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 274 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 4.5667 | 0.017033 | 0.23846 | 33325 | 152184.1667
3154073 | Transient fault | 2025-03-07 20:07 | 2024 | 2025-03-07 20:13 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.1 | 0.00037299 | 0.0052219 | 31280 | 3128
2987129 | Transient fault | 2023-02-22 08:53 | 2022 | 2023-02-22 08:55 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.033333 | 0.00012433 | 0.0017406 | 33290 | 1109.6667
3100014 | TRANSIENT FAULT | 2024-06-27 19:23 | 2023 | 2024-06-27 19:25 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 0.033333 | 0.00012433 | 0.0017406 | 33325 | 1110.8333
3079034 | Soweto ex Langata off byd AY 5302 awaiting operator, Karen office informed | 2024-04-04 05:57 | 2023 | 2024-04-04 06:00 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | SUSTAINED FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.05 | 0.0001865 | 0.0026109 | 33325 | 1666.25
3079338 | Transient fault | 2024-04-04 23:08 | 2023 | 2024-04-04 23:18 | Trip of Circuit Breaker/ Auto Reclosure | LOSS OF SUPPLY | TRANSIENT 11KV LINE FAULT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.16667 | 0.00062165 | 0.0087031 | 33325 | 5554.1667
3026353 | Single phasing. Suspected broken jumper | 2023-08-20 17:21 | 2023 | 2023-08-20 18:01 | Dim Lights | IRREGULAR SUPPLY | DIM LIGHTS | Resolved | Nairobi | Nairobi West County | Non Programmed | 40 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 0.66667 | 0.00064207 | 0.0089889 | 1967 | 1311.3333
3157779 | Single phasing | 2025-03-20 14:43 | 2024 | 2025-03-20 18:33 | Dim Lights | IRREGULAR SUPPLY | DIM LIGHTS | Resolved | Nairobi | Nairobi West County | Non Programmed | 230 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 3.8333 | 0.0026561 | 0.037186 | 1206 | 4623
3174232 | Report of Dim lights | 2025-05-26 19:00 | 2024 | 2025-05-26 20:48 | Dim Lights | IRREGULAR SUPPLY | DIM LIGHTS | Resolved | Nairobi | Nairobi West County | Non Programmed | 108 | 2905.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 1.8 | 0.0052301 | 0.073221 | 12217 | 21990.6
3026134 | Single phasing on Soweto ex Langata and LBS AY5179 not closing on SCADA. | 2023-08-18 19:11 | 2023 | 2023-08-19 10:38 | Dim Lights | IRREGULAR SUPPLY | DIM LIGHTS | Resolved | Nairobi | Nairobi West County | Non Programmed | 927 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 15.45 | 0.057627 | 0.80678 | 33295 | 514407.75
3141030 | Hardy ex Langata controlled byd AY 1104 due to fallen pole to Girraffe centre | 2025-01-11 20:38 | 2024 | 2025-01-11 20:58 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.33333 | 0.0005021 | 0.0070294 | 2958 | 986
3013673 | Replace a faulty VT at AY5254 | 2023-06-13 12:13 | 2022 | 2023-06-13 13:40 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 87 | 1506.3 | 2649 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 1.45 | 0.0021841 | 0.030578 | 2649 | 3841.05
3063647 | To replace VTs at AY5254 | 2024-01-31 14:42 | 2023 | 2024-01-31 15:02 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.33333 | 0.0005021 | 0.0070294 | 2807 | 935.6667
3299987 | Hardy ex Langata controlled to repair broken jumper at AY 1104 | 2026-03-31 17:21 | 2025 | 2026-03-31 17:47 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 26 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.43333 | 0.00087382 | 0.012233 | 3056 | 1324.2667
3127618 | Controlled to close ABS Y 172 | 2024-11-11 12:09 | 2024 | 2024-11-11 12:17 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 0.13333 | 0.00020084 | 0.0028118 | 2958 | 394.4
3036384 | switching operation. | 2023-10-02 19:41 | 2023 | 2023-10-02 20:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 19 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.31667 | 0.000477 | 0.0066779 | 2654 | 840.4333
2943540 | Local testing of AY1118 with closing failure | 2022-08-02 11:11 | 2022 | 2022-08-02 11:12 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 0.016667 | 2.5105e-05 | 0.00035147 | 2406 | 40.1
3120225 | Trace maintenance | 2024-10-09 08:30 | 2024 | 2024-10-09 17:42 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 552 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 9.2 | 0.013858 | 0.19401 | 2958 | 27213.6
3192003 | controlled | 2025-08-28 10:31 | 2025 | 2025-08-28 11:23 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 52 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.86667 | 0.0017476 | 0.024467 | 3000 | 2600
3203550 | Controlled | 2025-10-18 21:40 | 2025 | 2025-10-18 21:52 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.2 | 0.0004033 | 0.0056462 | 3000 | 600
3101323 | Trace maintenance | 2024-07-05 08:00 | 2024 | 2024-07-05 19:04 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 664 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 11.0667 | 0.01667 | 0.23338 | 2832 | 31340.8
3089936 | controlled | 2024-05-12 11:02 | 2023 | 2024-05-12 11:34 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 32 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.53333 | 0.00080336 | 0.011247 | 2832 | 1510.4
3087448 | Hardy ex Langata controlled byd AY 113 to introduce mid-span pole to avert poor | 2024-05-03 12:38 | 2023 | 2024-05-03 16:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 252 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 4.2 | 0.0063265 | 0.08857 | 2832 | 11894.4
3058979 | CONTROLLED | 2024-01-08 16:04 | 2023 | 2024-01-08 18:14 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 130 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 2.1667 | 0.0032636 | 0.045691 | 2807 | 6081.8333
3134225 | controlled | 2024-12-08 11:40 | 2024 | 2024-12-08 14:55 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 195 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 3.25 | 0.0048955 | 0.068537 | 2958 | 9613.5
2990977 | Hardy ex Langata controlled to repair jumper at cable take off | 2023-03-11 11:00 | 2022 | 2023-03-11 14:25 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 205 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 3.4167 | 0.0051465 | 0.072051 | 2561 | 8750.0833
3082928 | Controlled | 2024-04-18 11:49 | 2023 | 2024-04-18 12:24 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 35 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.58333 | 0.00087867 | 0.012301 | 2832 | 1652
3101122 | controlled | 2024-07-04 07:19 | 2024 | 2024-07-04 18:10 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 651 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 10.85 | 0.016343 | 0.22881 | 2832 | 30727.2
3040080 | Controlled | 2023-10-19 11:03 | 2023 | 2023-10-19 14:24 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 201 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 3.35 | 0.0032264 | 0.045169 | 1967 | 6589.45
2985212 | Kuwinda ex Langata controlled to link burnt HT fuse spur to Mokoiyet. | 2023-02-14 00:21 | 2022 | 2023-02-14 00:25 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.066667 | 6.4207e-05 | 0.00089889 | 1922 | 128.1333
2984163 | Controlled for clearance on Karen Hospital | 2023-02-08 13:04 | 2022 | 2023-02-08 13:13 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.15 | 0.00014447 | 0.0020225 | 1922 | 288.3
2975638 | Controlled to carry out repairs | 2022-12-27 16:50 | 2022 | 2022-12-27 17:45 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 55 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.91667 | 0.00088284 | 0.01236 | 1922 | 1761.8333
3068905 | controlled | 2024-02-22 21:30 | 2023 | 2024-02-22 21:31 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 0.016667 | 1.6052e-05 | 0.00022472 | 1991 | 33.1833
3105398 | Trace maintenance | 2024-07-26 08:29 | 2024 | 2024-07-26 17:13 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 524 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 8.7333 | 0.0084111 | 0.11776 | 2020 | 17641.3333
3015068 | Clearance to remove a tree branch on Karen Hospital feeder | 2023-06-19 19:45 | 2022 | 2023-06-19 19:49 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 963.1 | 1938 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.066667 | 6.4207e-05 | 0.00089889 | 1938 | 129.2
3105617 | controlled | 2024-07-27 13:41 | 2024 | 2024-07-27 13:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.15 | 0.00014447 | 0.0020225 | 2020 | 303
3116966 | Controlled to repair broken jumper | 2024-09-25 12:04 | 2024 | 2024-09-25 12:52 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 1656 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.8 | 0.0013248 | 0.018547 | 2020 | 1616
3159171 | Controlled for clearance on Karen Hospital feeder | 2025-03-25 12:52 | 2024 | 2025-03-25 13:01 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.15 | 0.00014447 | 0.0020225 | 2155 | 323.25
2990107 | To bypass AY5306 | 2023-03-07 18:37 | 2022 | 2023-03-07 20:40 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | -19 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | -0.31667 | -0.00030498 | -0.0042697 | 1922 | -608.6333
3028197 | CONTROLLED | 2023-08-29 18:42 | 2023 | 2023-08-29 19:06 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 24 | 963.1 | 1967 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 0.4 | 0.00038524 | 0.0053934 | 1967 | 786.8
3122585 | controlled | 2024-10-19 15:19 | 2024 | 2024-10-19 17:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 101 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 1.6833 | 0.0016212 | 0.022697 | 2139 | 3600.65
3112703 | Kuwinda ex Langata controlled byd AY 5306 for trace maintenance. | 2024-09-04 07:31 | 2024 | 2024-09-04 16:58 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 567 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 9.45 | 0.0091013 | 0.12742 | 2020 | 19089
3190377 | Contolled | 2025-08-16 07:29 | 2025 | 2025-08-16 17:18 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 589 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 9.8167 | 0.0094544 | 0.13236 | 1796 | 17630.7333
2984948 | Kuwinda ex Langata controlled to link HT spur to Mokoiyet. | 2023-02-12 23:37 | 2022 | 2023-02-12 23:47 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 0.16667 | 0.00016052 | 0.0022472 | 1922 | 320.3333
3149703 | Incidence no: 3149703 has automatically been generated from shutdown no: 82993 | 2025-02-18 09:00 | 2024 | 2025-02-18 16:11 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Programmed | 431 | 963.1 | 2139 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 7.1833 | 0.0069183 | 0.096856 | 2139 | 15365.15
3143355 | Controlled due to fire incidence at Silanga Rd | 2025-01-22 14:56 | 2024 | 2025-01-22 15:41 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 45 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.75 | 0.00051968 | 0.0072755 | 1188 | 891
3013718 | Replace a faulty VT at AY5140 | 2023-06-13 14:19 | 2022 | 2023-06-13 15:01 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 42 | 692.9 | 1059 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.7 | 0.00048503 | 0.0067904 | 1059 | 741.3
3178708 | Inspection of AY122 for malfunction | 2025-06-18 14:42 | 2024 | 2025-06-18 14:48 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.1 | 8.542e-05 | 0.0011959 | 1206 | 120.6
3190381 | Controlled | 2025-08-16 08:08 | 2025 | 2025-08-16 17:18 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 550 | 0 | 0 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 9.1667 | 0 | 0 | 0 | 0
2953587 | controlled | 2022-09-18 20:38 | 2022 | 2022-09-18 20:49 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 692.9 | 872 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 0.18333 | 0.00012703 | 0.0017784 | 872 | 159.8667
3124843 | controlled | 2024-10-30 09:21 | 2024 | 2024-10-30 17:05 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 464 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 7.7333 | 0.0053584 | 0.075018 | 1188 | 9187.2
3132020 | controlled | 2024-11-29 10:10 | 2024 | 2024-11-29 16:22 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 372 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 6.2 | 0.004296 | 0.060144 | 1188 | 7365.6
3111742 | Trace maintenance | 2024-08-30 07:45 | 2024 | 2024-08-30 17:51 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 606 | 692.9 | 1092 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 10.1 | 0.0069983 | 0.097976 | 1092 | 11029.2
3155590 | Controlled | 2025-03-12 13:39 | 2024 | 2025-03-12 15:11 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 92 | 121.4 | 243 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.5333 | 0.00018615 | 0.0026061 | 243 | 372.6
2972705 | Faulty cable lug at Galeria | 2022-12-12 10:43 | 2022 | 2022-12-12 11:33 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.83333 | 0.0023431 | 0.032803 | 5212 | 4343.3333
3166666 | Magadi ex Langata controlled-spur to Muiri Rd to erect midspan HT pole | 2025-04-23 14:04 | 2024 | 2025-04-23 17:27 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 203 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 3.3833 | 0.0095129 | 0.13318 | 5774 | 19535.3667
3063669 | Replace VTs at AY100 and AY145 | 2024-01-31 15:50 | 2023 | 2024-01-31 17:35 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 105 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.75 | 0.0049205 | 0.068887 | 5343 | 9350.25
3138209 | controlled | 2024-12-26 12:34 | 2024 | 2024-12-26 13:59 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 85 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 1.4167 | 0.0039832 | 0.055765 | 5760 | 8160
2956448 | Broken jumper at KWS | 2022-10-01 20:30 | 2022 | 2022-10-01 20:52 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.36667 | 0.001031 | 0.014433 | 5016 | 1839.2
3206215 | controlled | 2025-10-29 10:35 | 2025 | 2025-10-29 10:41 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.1 | 0.00028117 | 0.0039364 | 6310 | 631
3262288 | Contolled | 2026-03-12 13:24 | 2025 | 2026-03-12 14:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 86 | 2811.7 | 6841 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 1.4333 | 0.0040301 | 0.056421 | 6841 | 9805.4333
3207184 | CONTROLLED | 2025-11-01 13:45 | 2025 | 2025-11-01 14:39 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 54 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.9 | 0.0025305 | 0.035427 | 6310 | 5679
3245675 | Controlled | 2026-02-18 16:40 | 2025 | 2026-02-18 16:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.16667 | 0.00046862 | 0.0065606 | 6310 | 1051.6667
3227335 | To link spur to Muiri close s/s 16080 | 2026-01-07 15:28 | 2025 | 2026-01-07 15:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.36667 | 0.001031 | 0.014433 | 6310 | 2313.6667
3131554 | controlled | 2024-11-27 16:10 | 2024 | 2024-11-27 17:30 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 80 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 1.3333 | 0.0037489 | 0.052485 | 5760 | 7680
3188452 | controlled | 2025-08-10 10:22 | 2025 | 2025-08-10 10:52 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 30 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.5 | 0.0014058 | 0.019682 | 6310 | 3155
3159500 | Switching operation - backfeed | 2025-03-26 10:33 | 2024 | 2025-03-26 10:37 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.066667 | 0.00018745 | 0.0026243 | 5774 | 384.9333
3183319 | controlled | 2025-07-14 12:44 | 2025 | 2025-07-14 12:46 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 1 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.016667 | 4.6862e-05 | 0.00065606 | 6310 | 105.1667
3072239 | To restore s/s 4518 - Bomas of Kenya | 2024-03-07 09:16 | 2023 | 2024-03-07 14:17 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 301 | 2811.7 | 5674 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 5.0167 | 0.014105 | 0.19748 | 5674 | 28464.5667
3095816 | Magadi rd ex Langata controlled for general maintenance(Boresha) | 2024-06-07 09:07 | 2023 | 2024-06-07 11:26 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 139 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 2.3167 | 0.0065138 | 0.091193 | 5690 | 13181.8333
3089920 | CONTROLLED | 2024-05-12 09:42 | 2023 | 2024-05-12 10:37 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 55 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.91667 | 0.0025774 | 0.036083 | 5690 | 5215.8333
2939547 | controlled | 2022-07-14 20:24 | 2022 | 2022-07-14 21:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 36 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.6 | 0.001687 | 0.023618 | 5016 | 3009.6
3159675 | Magadi ex Langata controlled to facilitate Hotline team in erecting HV pole- Lin | 2025-03-27 09:52 | 2024 | 2025-03-27 18:33 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 521 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 8.6833 | 0.024415 | 0.34181 | 5774 | 50137.5667
3088064 | Controlled | 2024-05-05 16:21 | 2023 | 2024-05-05 16:26 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.05 | 0.00014059 | 0.0019682 | 5690 | 284.5
2960198 | controlled | 2022-10-18 22:44 | 2022 | 2022-10-18 22:48 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 4 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.066667 | 0.00018745 | 0.0026243 | 5212 | 347.4667
3215958 | Magadi ex Langata controlled to cut trees | 2025-12-09 12:39 | 2025 | 2025-12-09 14:23 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 104 | 2849.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 1.7333 | 0.0049395 | 0.069153 | 6310 | 10937.3333
3188524 | controlled | 2025-08-10 14:58 | 2025 | 2025-08-10 15:39 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 41 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.68333 | 0.0019213 | 0.026899 | 6310 | 4311.8333
3108138 | general maintenance | 2024-08-11 10:03 | 2024 | 2024-08-11 15:33 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 330 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 5.5 | 0.015464 | 0.2165 | 5690 | 31295
3173512 | controlled | 2025-05-23 12:19 | 2024 | 2025-05-23 12:41 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.36667 | 0.001031 | 0.014433 | 5774 | 2117.1333
3134619 | controlled | 2024-12-10 09:33 | 2024 | 2024-12-10 17:09 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 456 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 7.6 | 0.021369 | 0.29916 | 5760 | 43776
3072351 | For clearance to finalise works on s/s 4518 | 2024-03-07 11:06 | 2023 | 2024-03-07 12:20 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 74 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 1.2333 | 0.003533 | 0.049462 | 12107 | 14931.9667
3082931 | Controlled | 2024-04-18 11:56 | 2023 | 2024-04-18 13:05 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 69 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.15 | 0.0032943 | 0.04612 | 12107 | 13923.05
3216348 | Controlled | 2025-12-10 17:13 | 2025 | 2025-12-10 17:27 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 0.23333 | 0.00067797 | 0.0094916 | 12796 | 2985.7333
3190558 | Contolled | 2025-08-19 11:54 | 2025 | 2025-08-19 13:16 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 82 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 1.3667 | 0.003971 | 0.055594 | 12796 | 17487.8667
3258570 | controlled | 2026-03-08 10:16 | 2025 | 2026-03-08 10:44 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 28 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.46667 | 0.0013559 | 0.018983 | 12796 | 5971.4667
3228413 | controlled | 2026-01-11 14:32 | 2025 | 2026-01-11 17:02 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 150 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 2.5 | 0.007264 | 0.1017 | 12796 | 31990
3190733 | Controlled | 2025-08-20 11:00 | 2025 | 2025-08-20 11:29 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 29 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.48333 | 0.0014044 | 0.019661 | 12796 | 6184.7333
3183318 | controlled | 2025-07-14 12:37 | 2025 | 2025-07-14 12:45 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.13333 | 0.00038741 | 0.0054238 | 12796 | 1706.1333
2980021 | Broken jumper byd AY137 | 2023-01-18 06:59 | 2022 | 2023-01-18 12:09 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 310 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2023 | 5.1667 | 0.0148 | 0.20721 | 11953 | 61757.1667
3069895 | Replace oiltype VTS with Airtype VTS - Y137,Y2099,Y195 and Y169 | 2024-02-27 11:25 | 2023 | 2024-02-27 14:48 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 203 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 3.3833 | 0.0096919 | 0.13569 | 12066 | 40823.3
3144173 | Link spur to Royal paint | 2025-01-25 13:09 | 2024 | 2025-01-25 13:14 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.083333 | 0.00023872 | 0.003342 | 12297 | 1024.75
3089922 | CONTROLLED | 2024-05-12 09:51 | 2023 | 2024-05-12 13:27 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 216 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 3.6 | 0.010313 | 0.14438 | 12107 | 43585.2
3125241 | controlled | 2024-10-31 19:38 | 2024 | 2024-10-31 20:51 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 73 | 2864.6 | 12291 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 1.2167 | 0.0034853 | 0.048794 | 12291 | 14954.05
3125040 | Trace maintenance | 2024-10-31 08:48 | 2024 | 2024-10-31 18:01 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 553 | 2864.6 | 12291 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 9.2167 | 0.026402 | 0.36963 | 12291 | 113282.05
3112928 | Ngei ex Langata controlled byd AY 195 to repair broken jumper | 2024-09-04 21:09 | 2024 | 2024-09-04 21:09 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 0 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0 | 0 | 0 | 12107 | 0
3136396 | controlled | 2024-12-18 11:27 | 2024 | 2024-12-18 13:03 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 96 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 1.6 | 0.0045834 | 0.064167 | 12297 | 19675.2
2957039 | Restore s/s 14406 with broken links | 2022-10-04 12:50 | 2022 | 2022-10-04 12:57 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2864.6 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.1 | 0.00028646 | 0.0040104 | 11799 | 1179.9
3237239 | Controlled | 2026-02-03 13:02 | 2025 | 2026-02-03 13:49 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 47 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.78333 | 0.0022761 | 0.031865 | 12796 | 10023.5333
3061791 | Controlled | 2024-01-22 17:18 | 2023 | 2024-01-22 17:24 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 2864.6 | 12066 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 0.1 | 0.00028646 | 0.0040104 | 12066 | 1206.6
3077711 | BYD AY 195 | 2024-03-28 21:32 | 2023 | 2024-03-28 21:50 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 18 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 0.3 | 0.00085938 | 0.012031 | 12107 | 3632.1
2998494 | Replace VT on AY137 | 2023-04-06 14:14 | 2022 | 2023-04-06 15:05 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.85 | 0.0024349 | 0.034089 | 11953 | 10160.05
3106061 | Controlled | 2024-07-30 08:36 | 2024 | 2024-07-30 17:08 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 512 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 8.5333 | 0.016682 | 0.23355 | 837 | 7142.4
3020402 | Transient fault | 2023-07-19 14:16 | 2023 | 2023-07-19 14:19 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 3 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.05 | 9.7745e-05 | 0.0013684 | 763 | 38.15
3063653 | Replace VTs at AY105 | 2024-01-31 15:20 | 2023 | 2024-01-31 16:32 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 72 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.2 | 0.0023459 | 0.032842 | 796 | 955.2
3351714 | controlled | 2026-04-19 13:21 | 2025 | 2026-04-19 14:18 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 57 | 1954.9 | 1007 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.95 | 0.0018572 | 0.026 | 1007 | 956.65
3036388 | switching operation. | 2023-10-02 19:41 | 2023 | 2023-10-02 20:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 19 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.31667 | 0.00061905 | 0.0086667 | 763 | 241.6167
3105869 | Ndalat ex langata controlled for trace maintenance | 2024-07-29 09:55 | 2024 | 2024-07-29 17:54 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 479 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 7.9833 | 0.015607 | 0.21849 | 837 | 6682.05
3252803 | controlled | 2026-02-28 14:10 | 2025 | 2026-02-28 14:52 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 42 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.7 | 0.0013684 | 0.019158 | 988 | 691.6
3033469 | controlled | 2023-09-21 14:27 | 2023 | 2023-09-21 15:13 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 46 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.76667 | 0.0014988 | 0.020983 | 763 | 584.9667
3095810 | Ndalat ex Langata controlled byd Y5396 for trace maintenance | 2024-06-07 08:39 | 2023 | 2024-06-07 18:53 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 614 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 10.2333 | 0.020005 | 0.28007 | 837 | 8565.3
3084721 | Shutdown Ref; E21532023070021 | 2024-04-24 11:50 | 2023 | 2024-04-24 13:19 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 89 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.4833 | 0.0028998 | 0.040597 | 837 | 1241.55
3105921 | Ndalat ex Langata controlled to repair AY 5253 | 2024-07-29 13:51 | 2024 | 2024-07-29 14:45 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 54 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.9 | 0.0017594 | 0.024632 | 837 | 753.3
3144907 | Repair AY5254 | 2025-01-28 10:56 | 2024 | 2025-01-28 11:44 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 1954.9 | 925 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.8 | 0.0015639 | 0.021895 | 925 | 740
3106358 | Controlled | 2024-07-31 09:43 | 2024 | 2024-07-31 16:13 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 390 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 6.5 | 0.012707 | 0.1779 | 837 | 5440.5
3119998 | Trace maintenance | 2024-10-08 09:24 | 2024 | 2024-10-08 17:36 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 492 | 1954.9 | 924 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 8.2 | 0.01603 | 0.22442 | 924 | 7576.8
2998498 | To install VT at AY5253 | 2023-04-06 15:38 | 2022 | 2023-04-06 16:30 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 0.16667 | 0.00032582 | 0.0045614 | 724 | 120.6667
3097752 | Ndalat ex Langata byd AY 119 controlled to repair broken jumper at AY 119 | 2024-06-17 11:07 | 2023 | 2024-06-17 11:16 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 0.15 | 0.00029323 | 0.0041053 | 837 | 125.55
3189654 | Ndalat ex Langata controlled for trace maintenance | 2025-08-15 07:38 | 2025 | 2025-08-15 17:17 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 579 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 9.65 | 0.018865 | 0.26411 | 988 | 9534.2
3121334 | controlled | 2024-10-14 14:27 | 2024 | 2024-10-14 14:29 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 2 | 1954.9 | 924 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 0.033333 | 6.5163e-05 | 0.00091229 | 924 | 30.8
3142311 | controlled | 2025-01-17 13:45 | 2024 | 2025-01-17 15:58 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 133 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 2.2167 | 0.0082679 | 0.11575 | 32702 | 72489.4333
3142136 | Load management | 2025-01-16 19:23 | 2024 | 2025-01-16 20:36 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 73 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 1.2167 | 0.004538 | 0.063533 | 32702 | 39787.4333
3081430 | Soweto ex Langata controlled to repair broken jumper | 2024-04-12 13:58 | 2023 | 2024-04-12 15:04 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 66 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.1 | 0.0041029 | 0.05744 | 33325 | 36657.5
3155360 | Controlled | 2025-03-11 18:39 | 2024 | 2025-03-11 20:45 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 126 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.1 | 0.0078328 | 0.10966 | 31280 | 65688
3188410 | Controlled to mitigate losses | 2025-08-10 06:46 | 2025 | 2025-08-10 14:21 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 455 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 7.5833 | 0.028285 | 0.39599 | 27872 | 211362.6667
3176867 | energy loss due to vandalism | 2025-06-10 08:00 | 2024 | 2025-06-11 21:39 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 2259 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 37.65 | 0.14043 | 1.966 | 31280 | 1177692
3067646 | controlled | 2024-02-18 12:49 | 2023 | 2024-02-18 13:49 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 60 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 1 | 0.0037299 | 0.052219 | 33331 | 33331
3212384 | controlled | 2025-11-22 17:45 | 2025 | 2025-11-22 18:35 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 0.83333 | 0.0031082 | 0.043515 | 27872 | 23226.6667
3206888 | controlled | 2025-10-31 12:00 | 2025 | 2025-10-31 13:07 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 1.1167 | 0.0041651 | 0.058311 | 27872 | 31123.7333
3249281 | Controlled for load shedding due to loss of wind | 2026-02-23 19:12 | 2025 | 2026-02-23 20:57 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 105 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.75 | 0.0065273 | 0.091383 | 27872 | 48776
3202006 | To megger s/s 109040 200Kva Tx | 2025-10-11 12:57 | 2025 | 2025-10-11 13:59 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 61 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 1.0167 | 0.0037921 | 0.053089 | 27872 | 28336.5333
3201271 | Repair CT's cable on the relay | 2025-10-08 10:43 | 2025 | 2025-10-08 14:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 197 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 3.2833 | 0.012247 | 0.17145 | 27872 | 91513.0667
3236435 | Controlled | 2026-02-01 14:54 | 2025 | 2026-02-01 15:04 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.16667 | 0.00062165 | 0.0087031 | 27872 | 4645.3333
3000970 | Soweto ex Langata controlled to replace burnt pole beyond AY5050. | 2023-04-15 11:17 | 2022 | 2023-04-15 15:10 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 233 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 3.8833 | 0.014484 | 0.20278 | 33290 | 129276.1667
3031119 | controlled to repalce faulty VTs at AY5367 | 2023-09-11 17:06 | 2023 | 2023-09-11 18:00 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 54 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.9 | 0.0033569 | 0.046997 | 33295 | 29965.5
3171895 | Controlled due to fire incidence | 2025-05-15 17:24 | 2024 | 2025-05-16 17:34 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 1450 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 24.1667 | 0.090139 | 1.2619 | 31280 | 755933.3333
3167247 | controlled | 2025-04-25 10:30 | 2024 | 2025-04-25 11:11 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 41 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.68333 | 0.0025488 | 0.035683 | 31280 | 21374.6667
3072262 | For clearance to finalise works on s/s 4518 | 2024-03-07 11:10 | 2023 | 2024-03-07 12:22 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 72 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2024 | 1.2 | 0.0044759 | 0.062662 | 33325 | 39990
3014470 | To repair LBS 5300 | 2023-06-16 13:44 | 2022 | 2023-06-16 14:35 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.85 | 0.0031704 | 0.044386 | 33284 | 28291.4
3106979 | CONTROLLED | 2024-08-04 10:35 | 2024 | 2024-08-04 11:05 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 30 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 0.5 | 0.0018649 | 0.026109 | 33325 | 16662.5
3160049 | Soweto ex Langata controlled to repair broken jumper byd AY 5300 | 2025-03-28 14:20 | 2024 | 2025-03-28 15:22 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 62 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.0333 | 0.0038542 | 0.053959 | 31280 | 32322.6667
3084722 | Controlled for clearance | 2024-04-24 12:12 | 2023 | 2024-04-24 17:07 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 295 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 4.9167 | 0.018339 | 0.25674 | 33325 | 163847.9167
2975429 | controlled | 2022-12-26 11:17 | 2022 | 2022-12-26 11:39 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.36667 | 0.0013676 | 0.019147 | 33290 | 12206.3333
3134657 | controlled | 2024-12-10 10:50 | 2024 | 2024-12-10 16:54 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 364 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 6.0667 | 0.022628 | 0.31679 | 32702 | 198392.1333
3063313 | controlled | 2024-01-30 09:04 | 2023 | 2024-01-30 14:27 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 323 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 5.3833 | 0.020079 | 0.28111 | 33331 | 179431.8833
3112393 | Soweto ex langata controlled to repair broken jumper at Y 5298 | 2024-09-02 16:56 | 2024 | 2024-09-02 17:24 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 28 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 0.46667 | 0.0017406 | 0.024369 | 33325 | 15551.6667
3096504 | To repair AY5050 | 2024-06-10 14:15 | 2023 | 2024-06-10 14:35 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 20 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2024 | 0.33333 | 0.0012433 | 0.017406 | 33325 | 11108.3333
3156170 | Soweto ex Langata controlled byd Y 5060 to work on isolated section of Ngong Rd | 2025-03-14 12:50 | 2024 | 2025-03-14 19:31 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 401 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 6.6833 | 0.024928 | 0.34899 | 31280 | 209054.6667
3101528 | controlled | 2024-07-06 11:33 | 2024 | 2024-07-06 11:43 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.16667 | 0.00062165 | 0.0087031 | 33325 | 5554.1667
3125042 | Trace maintenance | 2024-10-31 08:48 | 2024 | 2024-10-31 20:51 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 723 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 12.05 | 0.044945 | 0.62923 | 32679 | 393781.95
3119018 | Soweto and Ngei ex Langata controlled to do trace maintenance | 2024-10-03 09:43 | 2024 | 2024-10-03 17:35 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 472 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 7.8667 | 0.029342 | 0.41079 | 32679 | 257074.8
2987115 | Replace a faulty VT at AY5179 | 2023-02-22 10:45 | 2022 | 2023-02-22 12:10 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 85 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 1.4167 | 0.005284 | 0.073976 | 33290 | 47160.8333
2952291 | For clearance to replace faulty TX at s/s 109040 | 2022-09-12 14:39 | 2022 | 2022-09-12 16:01 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED FOR CLEARANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 82 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 1.3667 | 0.0050975 | 0.071365 | 32658 | 44632.6
3089989 | To repair AY5302 | 2024-05-12 13:47 | 2023 | 2024-05-12 14:30 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SYSTEM OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 43 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.71667 | 0.0026731 | 0.037423 | 33325 | 23882.9167
3351999 | controlled | 2026-04-19 15:53 | 2025 | 2026-04-19 18:05 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED SWITCHING OPERATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 132 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 2.2 | 0.0082058 | 0.11488 | 26342 | 57952.4
3239660 | controlled | 2026-02-07 19:08 | 2025 | 2026-02-07 19:37 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 29 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.48333 | 0.0018028 | 0.025239 | 27872 | 13471.4667
3050705 | Controlled | 2023-11-29 14:33 | 2023 | 2023-11-29 17:02 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 149 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 2.4833 | 0.0092626 | 0.12968 | 33331 | 82771.9833
3156782 | Replace faulty VTs at AY5050 | 2025-03-17 12:29 | 2024 | 2025-03-17 14:33 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 124 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.0667 | 0.0077085 | 0.10792 | 31280 | 64645.3333
2957232 | Soweto ex Langata Controlled to seperate twisted conductors | 2022-10-05 09:40 | 2022 | 2022-10-05 11:45 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 125 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 2.0833 | 0.0077706 | 0.10879 | 32658 | 68037.5
3155587 | Controlled | 2025-03-12 13:31 | 2024 | 2025-03-12 15:08 | Controlled System Operation | CONTROLLED INTERRUPTION | CONTROLLED TO CARRY OUT REPAIRS | Resolved | Nairobi | Nairobi West County | Non Programmed | 97 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.6167 | 0.00603 | 0.08442 | 31280 | 50569.3333
3256299 | Incidence no: 3256299 has automatically been generated from shutdown no: 90674 | 2026-03-05 09:55 | 2025 | 2026-03-05 17:10 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 435 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 7.25 | 0.01462 | 0.20467 | 3000 | 21750
3218068 | Incidence no: 3218068 has automatically been generated from shutdown no: 89347 | 2025-12-17 09:00 | 2025 | 2025-12-17 18:53 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 593 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 9.8833 | 0.01993 | 0.27902 | 3000 | 29650
3169491 | Incidence no: 3169491 has automatically been generated from shutdown no: 84532 | 2025-05-06 09:00 | 2024 | 2025-05-06 17:00 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE NEW CONNECTIONS | Resolved | Nairobi | Nairobi West County | Programmed | 480 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 8 | 0.01205 | 0.16871 | 2964 | 23712
2988484 | Incidence no: 2988484 has automatically been generated from shutdown no: 70989 | 2023-02-28 10:14 | 2022 | 2023-02-28 16:27 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 373 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 6.2167 | 0.0093642 | 0.1311 | 2561 | 15920.8833
2939446 | Incidence no: 2939446 has automatically been generated from shutdown no: 67887 | 2022-07-14 09:00 | 2022 | 2022-07-14 15:38 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 398 | 1506.3 | 2406 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 6.6333 | 0.0099918 | 0.13989 | 2406 | 15959.8
3162706 | Incidence no: 3162706 has automatically been generated from shutdown no: 84329 | 2025-04-08 08:59 | 2024 | 2025-04-08 16:00 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE NEW CONNECTIONS | Resolved | Nairobi | Nairobi West County | Programmed | 421 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 7.0167 | 0.010569 | 0.14797 | 2964 | 20797.4
3174693 | Incidence no: 3174693 has automatically been generated from shutdown no: 85181 | 2025-05-29 09:00 | 2024 | 2025-05-29 18:25 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE NEW CONNECTIONS | Resolved | Nairobi | Nairobi West County | Programmed | 565 | 2016.5 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 9.4167 | 0.018989 | 0.26584 | 2964 | 27911
2993242 | Incidence no: 2993242 has automatically been generated from shutdown no: 71445 | 2023-03-21 10:47 | 2022 | 2023-03-21 16:15 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 328 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 5.4667 | 0.0082344 | 0.11528 | 2561 | 14000.1333
2961901 | Incidence no: 2961901 has automatically been generated from shutdown no: 69387 | 2022-10-27 10:05 | 2022 | 2022-10-27 19:09 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 544 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 9.0667 | 0.013657 | 0.1912 | 2561 | 23219.7333
3168324 | Incidence no: 3168324 has automatically been generated from shutdown no: 84664 | 2025-04-30 11:22 | 2024 | 2025-04-30 18:37 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 435 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 7.25 | 0.010921 | 0.15289 | 2964 | 21489
3118717 | Incidence no: 3118717 has automatically been generated from shutdown no: 80874 | 2024-10-02 09:00 | 2024 | 2024-10-02 16:25 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 445 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 7.4167 | 0.011172 | 0.1564 | 2958 | 21938.5
3183736 | Incidence no: 3183736 has automatically been generated from shutdown no: 86076 | 2025-07-16 13:24 | 2025 | 2025-07-16 17:26 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 242 | 2016.5 | 3000 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 4.0333 | 0.0081332 | 0.11387 | 3000 | 12100
3240973 | Incidence no: 3240973 has automatically been generated from shutdown no: 90137 | 2026-02-10 09:00 | 2025 | 2026-02-10 18:20 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 560 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 9.3333 | 0.0089889 | 0.12585 | 1796 | 16762.6667
3202630 | Incidence no: 3202630 has automatically been generated from shutdown no: 88161 | 2025-10-14 09:00 | 2025 | 2025-10-14 15:20 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 380 | 963.1 | 1796 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 6.3333 | 0.0060996 | 0.085395 | 1796 | 11374.6667
2974496 | Incidence no: 2974496 has automatically been generated from shutdown no: 70081 | 2022-12-20 13:23 | 2022 | 2022-12-20 16:26 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 183 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 3.05 | 0.0029375 | 0.041124 | 1922 | 5862.1
3063562 | Incidence no: 3063562 has automatically been generated from shutdown no: 76580 | 2024-01-31 09:00 | 2023 | 2024-01-31 16:11 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 431 | 963.1 | 1991 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 7.1833 | 0.0069183 | 0.096856 | 1991 | 14302.0167
2982919 | Incidence no: 2982919 has automatically been generated from shutdown no: 70506 | 2023-02-02 09:02 | 2022 | 2023-02-02 17:27 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 505 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 8.4167 | 0.0081061 | 0.11349 | 1922 | 16176.8333
2991535 | Incidence no: 2991535 has automatically been generated from shutdown no: 71215 | 2023-03-14 09:42 | 2022 | 2023-03-14 17:17 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 455 | 963.1 | 1922 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 7.5833 | 0.0073035 | 0.10225 | 1922 | 14575.1667
3181642 | Incidence no: 3181642 has automatically been generated from shutdown no: 86035 | 2025-07-04 09:00 | 2025 | 2025-07-04 18:09 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 549 | 854.2 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 9.15 | 0.0078159 | 0.10942 | 1206 | 11034.9
3149704 | Incidence no: 3149704 has automatically been generated from shutdown no: 82992 | 2025-02-18 09:00 | 2024 | 2025-02-18 16:08 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 428 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 7.1333 | 0.0049427 | 0.069198 | 1188 | 8474.4
2982917 | Incidence no: 2982917 has automatically been generated from shutdown no: 70505 | 2023-02-02 09:02 | 2022 | 2023-02-02 17:35 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 505 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 8.4167 | 0.0058319 | 0.081647 | 1049 | 8829.0833
3063610 | Incidence no: 3063610 has automatically been generated from shutdown no: 76581 | 2024-01-31 09:00 | 2023 | 2024-01-31 12:46 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 226 | 692.9 | 1081 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 3.7667 | 0.0026099 | 0.036539 | 1081 | 4071.7667
3240970 | Incidence no: 3240970 has automatically been generated from shutdown no: 90131 | 2026-02-10 09:00 | 2025 | 2026-02-10 18:20 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 560 | 122.2 | 177 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 9.3333 | 0.0011405 | 0.015967 | 177 | 1652
3215897 | Incidence no: 3215897 has automatically been generated from shutdown no: 89226 | 2025-12-09 09:00 | 2025 | 2025-12-09 16:04 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 424 | 122.2 | 177 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2025 | 7.0667 | 0.00086355 | 0.01209 | 177 | 1250.8
2939463 | Incidence no: 2939463 has automatically been generated from shutdown no: 67885 | 2022-07-14 09:00 | 2022 | 2022-07-14 15:38 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 398 | 121.4 | 208 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 6.6333 | 0.00080529 | 0.011274 | 208 | 1379.7333
3019392 | Incidence no: 3019392 has automatically been generated from shutdown no: 72987 | 2023-07-13 10:42 | 2023 | 2023-07-13 16:07 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 325 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 5.4167 | 0.01523 | 0.21322 | 5260 | 28491.6667
3181470 | Incidence no: 3181470 has automatically been generated from shutdown no: 85882 | 2025-07-03 09:17 | 2025 | 2025-07-03 18:26 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 549 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 9.15 | 0.025727 | 0.36018 | 5774 | 52832.1
3052470 | Incidence no: 3052470 has automatically been generated from shutdown no: 75693 | 2023-12-07 10:16 | 2023 | 2023-12-07 14:39 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 263 | 2811.7 | 5343 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2023 | 4.3833 | 0.012325 | 0.17254 | 5343 | 23420.15
2961902 | Incidence no: 2961902 has automatically been generated from shutdown no: 69383 | 2022-10-27 10:08 | 2022 | 2022-10-27 19:09 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 541 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 9.0167 | 0.025352 | 0.35493 | 5212 | 46994.8667
3201370 | Planned outage S/N 87901 | 2025-10-08 09:30 | 2025 | 2025-10-08 16:32 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 422 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 7.0333 | 0.019776 | 0.27686 | 6310 | 44380.3333
3213507 | Incidence no: 3213507 has automatically been generated from shutdown no: 88924 | 2025-11-27 09:09 | 2025 | 2025-11-27 17:46 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 517 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 8.6167 | 0.024227 | 0.33918 | 6310 | 54371.1667
3041716 | Incidence no: 3041716 has automatically been generated from shutdown no: 75018 | 2023-10-27 09:00 | 2023 | 2023-10-27 15:05 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 365 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 6.0833 | 0.017105 | 0.23946 | 5260 | 31998.3333
3169507 | Incidence no: 3169507 has automatically been generated from shutdown no: 84782 | 2025-05-06 09:00 | 2024 | 2025-05-06 17:55 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 535 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 8.9167 | 0.025071 | 0.35099 | 5774 | 51484.8333
2974503 | Incidence no: 2974503 has automatically been generated from shutdown no: 70080 | 2022-12-20 14:22 | 2022 | 2022-12-20 17:18 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 176 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 2.9333 | 0.0082477 | 0.11547 | 5212 | 15288.5333
3164329 | Incidence no: 3164329 has automatically been generated from shutdown no: 84465 | 2025-04-14 09:55 | 2024 | 2025-04-14 18:20 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 505 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 8.4167 | 0.023665 | 0.33131 | 5774 | 48597.8333
2939450 | Incidence no: 2939450 has automatically been generated from shutdown no: 67884 | 2022-07-14 09:00 | 2022 | 2022-07-14 15:38 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 398 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 6.6333 | 0.018651 | 0.26111 | 5016 | 33272.8
3177299 | Incidence no: 3177299 has automatically been generated from shutdown no: 85454 | 2025-06-12 09:00 | 2024 | 2025-06-12 17:04 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 484 | 2811.7 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 8.0667 | 0.022681 | 0.31753 | 5774 | 46576.9333
3033337 | Incidence no: 3033337 has automatically been generated from shutdown no: 74270 | 2023-09-21 09:48 | 2023 | 2023-09-21 17:49 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 481 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 8.0167 | 0.02254 | 0.31557 | 5260 | 42167.6667
3251030 | Incidence no: 3251030 has automatically been generated from shutdown no: 90489 | 2026-02-26 09:00 | 2025 | 2026-02-26 16:34 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 454 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 7.5667 | 0.021986 | 0.3078 | 12796 | 96823.0667
3192704 | controlled | 2025-08-31 18:12 | 2025 | 2025-08-31 19:00 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 2905.6 | 12796 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.8 | 0.0023245 | 0.032543 | 12796 | 10236.8
3041025 | Incidence no: 3041025 has automatically been generated from shutdown no: 75015 | 2023-10-24 10:00 | 2023 | 2023-10-24 16:27 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 387 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 6.45 | 0.018477 | 0.25867 | 12031 | 77599.95
3033074 | Incidence no: 3033074 has automatically been generated from shutdown no: 74468 | 2023-09-20 09:00 | 2023 | 2023-09-20 16:15 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 435 | 2864.6 | 12031 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 7.25 | 0.020768 | 0.29076 | 12031 | 87224.75
2961449 | Incidence no: 2961449 has automatically been generated from shutdown no: 69366 | 2022-10-25 09:00 | 2022 | 2022-10-25 15:45 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 405 | 2864.6 | 11953 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 6.75 | 0.019336 | 0.2707 | 11953 | 80682.75
3163271 | Incidence no: 3163271 has automatically been generated from shutdown no: 84296 | 2025-04-10 09:00 | 2024 | 2025-04-10 18:45 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 585 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 9.75 | 0.01906 | 0.26684 | 933 | 9096.75
2985261 | Incidence no: 2985261 has automatically been generated from shutdown no: 70708 | 2023-02-14 09:29 | 2022 | 2023-02-14 16:45 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 436 | 1954.9 | 724 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 7.2667 | 0.014206 | 0.19888 | 724 | 5261.0667
3213246 | Incidence no: 3213246 has automatically been generated from shutdown no: 88919 | 2025-11-26 07:41 | 2025 | 2025-11-26 14:38 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 417 | 1954.9 | 988 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 6.95 | 0.013587 | 0.19021 | 988 | 6866.6
3178684 | Planned outage | 2025-06-18 10:05 | 2024 | 2025-06-18 16:49 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE NEW CONNECTIONS | Resolved | Nairobi | Nairobi West County | Non Programmed | 404 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 6.7333 | 0.013163 | 0.18428 | 933 | 6282.2
3026632 | Incidence no: 3026632 has automatically been generated from shutdown no: 73772 | 2023-08-22 10:48 | 2023 | 2023-08-22 16:28 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 340 | 1954.9 | 763 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 5.6667 | 0.011078 | 0.15509 | 763 | 4323.6667
3058904 | Incidence no: 3058904 has automatically been generated from shutdown no: 76265 | 2024-01-08 11:16 | 2023 | 2024-01-08 12:26 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 70 | 1954.9 | 796 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.1667 | 0.0022807 | 0.03193 | 796 | 928.6667
3156970 | Incidence no: 3156970 has automatically been generated from shutdown no: 83803 | 2025-03-18 09:00 | 2024 | 2025-03-18 13:13 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 253 | 1954.9 | 933 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 4.2167 | 0.0082432 | 0.1154 | 933 | 3934.15
3251028 | Incidence no: 3251028 has automatically been generated from shutdown no: 90488 | 2026-02-26 09:00 | 2025 | 2026-02-26 16:34 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 454 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 7.5667 | 0.028223 | 0.39512 | 27872 | 210898.1333
3037137 | Incidence no: 3037137 has automatically been generated from shutdown no: 74770 | 2023-10-06 10:55 | 2023 | 2023-10-06 15:13 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 258 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 4.3 | 0.016039 | 0.22454 | 33295 | 143168.5
3181168 | Incidence no: 3181168 has automatically been generated from shutdown no: 85779 | 2025-07-01 09:30 | 2025 | 2025-07-01 18:17 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Programmed | 527 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 8.7833 | 0.032761 | 0.45865 | 31280 | 274742.6667
2943171 | Planned outage | 2022-07-31 09:50 | 2022 | 2022-07-31 18:10 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE MAINTENANCE | Resolved | Nairobi | Nairobi West County | Non Programmed | 500 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 8.3333 | 0.031082 | 0.43516 | 32658 | 272150
3034474 | Load management due to generation shortfall | 2023-09-25 18:36 | 2023 | 2023-09-25 19:17 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 41 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 0.68333 | 0.0025488 | 0.035683 | 33295 | 22751.5833
3171129 | Load management | 2025-05-12 19:08 | 2024 | 2025-05-12 19:52 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 44 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.73333 | 0.0027353 | 0.038294 | 31280 | 22938.6667
3153136 | Controlled | 2025-03-03 19:06 | 2024 | 2025-03-03 22:06 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 180 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 3 | 0.01119 | 0.15666 | 31280 | 93840
3155344 | Controlled | 2025-03-11 18:08 | 2024 | 2025-03-12 00:03 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 355 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 5.9167 | 0.022069 | 0.30896 | 31280 | 185073.3333
3296697 | Load management | 2026-03-28 18:47 | 2025 | 2026-03-28 19:57 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 70 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 1.1667 | 0.0043516 | 0.060922 | 27892 | 32540.6667
3339604 | Load shedding due to generation shortfall | 2026-04-10 19:15 | 2025 | 2026-04-10 19:32 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.28333 | 0.0010568 | 0.014795 | 27892 | 7902.7333
3344801 | Load management due to generation shortfall | 2026-04-14 15:58 | 2025 | 2026-04-14 16:44 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 46 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.76667 | 0.0028596 | 0.040034 | 26342 | 20195.5333
3363089 | Load management | 2026-04-27 18:42 | 2025 | 2026-04-27 20:03 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 81 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 1.35 | 0.0050354 | 0.070495 | 26342 | 35561.7
3298878 | Load management due do generation shortion shortfall | 2026-03-30 18:55 | 2025 | 2026-03-30 20:48 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 113 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 1.8833 | 0.0070246 | 0.098345 | 27892 | 52529.9333
3346499 | Controlled | 2026-04-15 19:00 | 2025 | 2026-04-15 19:34 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 34 | 3729.9 | 26342 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 0.56667 | 0.0021136 | 0.029591 | 26342 | 14927.1333
3150088 | Load management due to generation shortfall | 2025-02-19 19:07 | 2024 | 2025-02-19 20:06 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 59 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.98333 | 0.0036677 | 0.051348 | 31280 | 30758.6667
3039645 | Load management | 2023-10-17 18:50 | 2023 | 2023-10-17 19:49 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 59 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.98333 | 0.0036677 | 0.051348 | 33295 | 32740.0833
3080670 | Load management | 2024-04-09 18:59 | 2023 | 2024-04-09 21:03 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 124 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 2.0667 | 0.0077085 | 0.10792 | 33325 | 68871.6667
3143121 | Load shedding due to generation shortfall | 2025-01-21 19:09 | 2024 | 2025-01-21 20:32 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 83 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 1.3833 | 0.0051597 | 0.072236 | 32702 | 45237.7667
3019103 | Load shedding due to generation shortfall. | 2023-07-11 19:38 | 2023 | 2023-07-11 20:29 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.85 | 0.0031704 | 0.044386 | 33295 | 28300.75
3185302 | Load shedding due to generation shortfall | 2025-07-24 19:07 | 2025 | 2025-07-24 19:33 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 26 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 0.43333 | 0.0016163 | 0.022628 | 27872 | 12077.8667
3189596 | Load shedding due to generation shortfall | 2025-08-14 19:13 | 2025 | 2025-08-14 20:04 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.85 | 0.0031704 | 0.044386 | 27872 | 23691.2
3173212 | Load shedding due to generation shortfall | 2025-05-21 18:52 | 2024 | 2025-05-21 19:45 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 53 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.88333 | 0.0032947 | 0.046126 | 31280 | 27630.6667
3088794 | Load management | 2024-05-07 18:48 | 2023 | 2024-05-07 20:20 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 92 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 1.5333 | 0.0057192 | 0.080069 | 33325 | 51098.3333
3079760 | Load shedding due to generation shortfall | 2024-04-06 18:55 | 2023 | 2024-04-06 19:43 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.8 | 0.0029839 | 0.041775 | 33325 | 26660
2941069 | Load management on Soweto ex Langata | 2022-07-21 19:20 | 2022 | 2022-07-21 21:49 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 149 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 2.4833 | 0.0092626 | 0.12968 | 32658 | 81100.7
2953809 | Load management due to high loads on Magadi line | 2022-09-19 19:04 | 2022 | 2022-09-19 22:04 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 180 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 3 | 0.01119 | 0.15666 | 32658 | 97974
3204650 | Load management due to generation shortfall | 2025-10-23 18:42 | 2025 | 2025-10-23 19:30 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 48 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.8 | 0.0029839 | 0.041775 | 27872 | 22297.6
3204906 | Load management on selected feeders ar Villa Franca, Ngong Rd, N/West, Langata s | 2025-10-24 15:53 | 2025 | 2025-10-24 16:15 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 0.36667 | 0.0013676 | 0.019147 | 27872 | 10219.7333
3204457 | controlled | 2025-10-22 18:19 | 2025 | 2025-10-22 20:58 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 159 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 2.65 | 0.0098842 | 0.13838 | 27872 | 73860.8
3213591 | Load shedding due to generation shortfall | 2025-11-27 18:56 | 2025 | 2025-11-27 20:15 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 79 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 1.3167 | 0.004911 | 0.068754 | 27872 | 36698.1333
3292410 | Load management generation shortfall | 2026-03-25 19:01 | 2025 | 2026-03-25 20:58 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 117 | 3729.9 | 27892 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 1.95 | 0.0072733 | 0.10183 | 27892 | 54389.4
3261477 | controlled | 2026-03-11 18:23 | 2025 | 2026-03-11 19:01 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 38 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.63333 | 0.0023623 | 0.033072 | 27872 | 17652.2667
3213879 | Load shedding due to generation shortfall | 2025-11-29 09:58 | 2025 | 2025-11-29 11:09 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 71 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2025 | 1.1833 | 0.0044137 | 0.061792 | 27872 | 32981.8667
3228221 | Load sheding | 2026-01-10 19:05 | 2025 | 2026-01-10 19:21 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 16 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.26667 | 0.00099464 | 0.013925 | 27872 | 7432.5333
3230953 | Controlled | 2026-01-18 19:01 | 2025 | 2026-01-18 19:08 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 7 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.11667 | 0.00043516 | 0.0060922 | 27872 | 3251.7333
3205689 | Load shedding due to generation shortfall | 2025-10-27 18:36 | 2025 | 2025-10-27 20:39 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 123 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 2.05 | 0.0076463 | 0.10705 | 27872 | 57137.6
3251642 | Controlled | 2026-02-26 18:29 | 2025 | 2026-02-26 20:26 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 117 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 1.95 | 0.0072733 | 0.10183 | 27872 | 54350.4
3204148 | Controlled | 2025-10-21 18:18 | 2025 | 2025-10-21 21:06 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 168 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2025 | 2.8 | 0.010444 | 0.14621 | 27872 | 78041.6
3237977 | Generation shortfall | 2026-02-04 19:18 | 2025 | 2026-02-04 19:26 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 8 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.13333 | 0.00049732 | 0.0069625 | 27872 | 3716.2667
3190490 | Controlled | 2025-08-16 19:04 | 2025 | 2025-08-16 20:02 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 58 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.96667 | 0.0036056 | 0.050478 | 27872 | 26942.9333
3190609 | Load shedding due to generation shortfall | 2025-08-19 19:12 | 2025 | 2025-08-19 20:34 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 82 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 1.3667 | 0.0050975 | 0.071365 | 27872 | 38091.7333
3193413 | Load shedding on selected feeders at N/South, Industrial, Ngong Rd and langata s | 2025-09-03 18:50 | 2025 | 2025-09-03 19:41 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 51 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2025 | 0.85 | 0.0031704 | 0.044386 | 27872 | 23691.2
3079010 | Controlled | 2024-04-03 19:40 | 2023 | 2024-04-03 20:04 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 24 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.4 | 0.001492 | 0.020887 | 33325 | 13330
3188179 | controlled | 2025-08-09 08:20 | 2025 | 2025-08-09 18:03 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 583 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 9.7167 | 0.036242 | 0.50739 | 27872 | 270822.9333
3174189 | Load management due to generation shortfall | 2025-05-26 17:47 | 2024 | 2025-05-26 17:53 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 6 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.1 | 0.00037299 | 0.0052219 | 31280 | 3128
3174197 | Load management due to generation shortfall | 2025-05-26 18:31 | 2024 | 2025-05-26 19:38 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 1.1167 | 0.0041651 | 0.058311 | 31280 | 34929.3333
3140036 | Load management | 2025-01-06 19:20 | 2024 | 2025-01-06 19:30 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.16667 | 0.00062165 | 0.0087031 | 32702 | 5450.3333
3088433 | Controlled | 2024-05-06 19:05 | 2023 | 2024-05-06 20:04 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 59 | 8869.3 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.98333 | 0.0087215 | 0.1221 | 33325 | 32769.5833
2972302 | Load management due to unavailability of generation | 2022-12-09 18:57 | 2022 | 2022-12-09 19:47 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 50 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 0.83333 | 0.0031082 | 0.043515 | 33290 | 27741.6667
3022020 | Load management | 2023-07-27 18:50 | 2023 | 2023-07-27 19:56 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 66 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 1.1 | 0.0041029 | 0.05744 | 33295 | 36624.5
3168838 | Transient fault | 2025-05-02 19:04 | 2024 | 2025-05-02 19:42 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 38 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.63333 | 0.0023623 | 0.033072 | 31280 | 19810.6667
3153813 | Load management on Soweto ex Langata byd AY 5179 | 2025-03-06 19:04 | 2024 | 2025-03-06 20:48 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 104 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.7333 | 0.0064652 | 0.090512 | 31280 | 54218.6667
3154992 | Load management due to generation shortfall | 2025-03-10 18:44 | 2024 | 2025-03-10 20:13 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 89 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.4833 | 0.0055327 | 0.077458 | 31280 | 46398.6667
3042242 | Load management due to loss of LTWP | 2023-10-30 10:37 | 2023 | 2023-10-30 10:46 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 9 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.15 | 0.00055948 | 0.0078328 | 33295 | 4994.25
3185636 | Load management | 2025-07-27 08:00 | 2025 | 2025-07-27 12:34 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 274 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2025 | 4.5667 | 0.017033 | 0.23846 | 27872 | 127282.1333
3187316 | Load management on selected fdrs at V/Franca,Langata,Ngong Road | 2025-08-04 19:25 | 2025 | 2025-08-04 19:53 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 28 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 0.46667 | 0.0017406 | 0.024369 | 27872 | 13006.9333
2940859 | Load management | 2022-07-20 19:29 | 2022 | 2022-07-20 22:34 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 185 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 3.0833 | 0.011501 | 0.16101 | 32658 | 100695.5
3178921 | Load shedding | 2025-06-19 19:23 | 2024 | 2025-06-19 20:02 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 39 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.65 | 0.0024244 | 0.033942 | 31280 | 20332
3020645 | Load management on Soweto ex Langata, Kibera ex Ngong Rd, Mogadishu and Kampala | 2023-07-20 17:21 | 2023 | 2023-07-20 17:35 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 14 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 0.23333 | 0.00087031 | 0.012184 | 33295 | 7768.8333
3012521 | Load management | 2023-06-07 18:56 | 2022 | 2023-06-07 19:43 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 47 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 0.78333 | 0.0029218 | 0.040905 | 33284 | 26072.4667
3020044 | Load management | 2023-07-17 19:08 | 2023 | 2023-07-17 20:22 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 74 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 1.2333 | 0.0046002 | 0.064403 | 33295 | 41063.8333
3018645 | Load management. | 2023-07-09 18:55 | 2023 | 2023-07-09 20:03 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 68 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 1.1333 | 0.0042272 | 0.059181 | 33295 | 37734.3333
3158820 | Load management | 2025-03-24 18:38 | 2024 | 2025-03-24 20:35 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 117 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.95 | 0.0072733 | 0.10183 | 31280 | 60996
3143448 | Load shedding | 2025-01-22 19:23 | 2024 | 2025-01-22 19:58 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 35 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.58333 | 0.0021758 | 0.030461 | 32702 | 19076.1667
3109980 | controlled | 2024-08-20 19:06 | 2024 | 2024-08-20 19:53 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 47 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 0.78333 | 0.0029218 | 0.040905 | 33325 | 26104.5833
3173375 | Load shedding due to generation shortfall | 2025-05-22 18:29 | 2024 | 2025-05-22 20:31 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 122 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 2.0333 | 0.0075841 | 0.10618 | 31280 | 63602.6667
3157454 | Controlled | 2025-03-19 18:58 | 2024 | 2025-03-19 20:50 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 112 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.8667 | 0.0069625 | 0.097475 | 31280 | 58389.3333
3157852 | Load management due to generation shortfall | 2025-03-20 19:10 | 2024 | 2025-03-20 22:15 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 185 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 3.0833 | 0.011501 | 0.16101 | 31280 | 96446.6667
3173825 | Load | 2025-05-24 18:58 | 2024 | 2025-05-24 19:50 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 52 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.86667 | 0.0032326 | 0.045256 | 31280 | 27109.3333
3131905 | Load management | 2024-11-28 18:54 | 2024 | 2024-11-28 20:01 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 67 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2024 | 1.1167 | 0.0041651 | 0.058311 | 32702 | 36517.2333
3118283 | Load management | 2024-09-30 19:22 | 2024 | 2024-09-30 23:54 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 272 | 3729.9 | 32679 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2024 | 4.5333 | 0.016909 | 0.23672 | 32679 | 148144.8
3103484 | Load shedding | 2024-07-15 19:07 | 2024 | 2024-07-15 20:06 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 59 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 0.98333 | 0.0036677 | 0.051348 | 33325 | 32769.5833
3079305 | Controlled | 2024-04-04 18:57 | 2023 | 2024-04-04 20:05 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 68 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.1333 | 0.0042272 | 0.059181 | 33325 | 37768.3333
3136512 | Load management due to generation shortfall | 2024-12-18 18:44 | 2024 | 2024-12-18 21:40 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 176 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2024 | 2.9333 | 0.010941 | 0.15317 | 32702 | 95925.8667
3168142 | Load management | 2025-04-29 19:03 | 2024 | 2025-04-29 19:56 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 53 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.88333 | 0.0032947 | 0.046126 | 31280 | 27630.6667
3170411 | Load shedding due to generation shortfall on selected feeders at Industrial,V/Fr | 2025-05-09 19:01 | 2024 | 2025-05-09 19:48 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 47 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 0.78333 | 0.0029218 | 0.040905 | 31280 | 24502.6667
3173632 | Load management | 2025-05-23 18:27 | 2024 | 2025-05-23 20:25 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 118 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2025 | 1.9667 | 0.0073355 | 0.1027 | 31280 | 61517.3333
3178442 | Load management on selected feeders:Soweto ex Langata,Kencell and Riverbank ex | 2025-06-17 19:14 | 2024 | 2025-06-17 19:43 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 29 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 0.48333 | 0.0018028 | 0.025239 | 31280 | 15118.6667
3165066 | Load management | 2025-04-16 18:57 | 2024 | 2025-04-16 19:15 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 18 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.3 | 0.001119 | 0.015666 | 31280 | 9384
3041431 | Loaad management due to generation shortfall | 2023-10-25 18:49 | 2023 | 2023-10-25 18:59 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2023 | 0.16667 | 0.00062165 | 0.0087031 | 33295 | 5549.1667
3020258 | Load management due to generation shortfall. | 2023-07-18 19:04 | 2023 | 2023-07-18 20:54 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 110 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2023 | 1.8333 | 0.0068382 | 0.095734 | 33295 | 61040.8333
3155371 | Load shedding due to generation shortfall | 2025-03-11 19:05 | 2024 | 2025-03-11 21:32 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 147 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.45 | 0.0091383 | 0.12794 | 31280 | 76636
3153507 | controlled | 2025-03-05 18:48 | 2024 | 2025-03-05 21:11 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 143 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.3833 | 0.0088896 | 0.12445 | 31280 | 74550.6667
3107047 | Load shedding on selected feeder due to loss of Gitaru 2 machines. | 2024-08-04 19:07 | 2024 | 2024-08-04 19:19 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2024 | 0.2 | 0.00074598 | 0.010444 | 33325 | 6665
3154226 | Load management on Soweto ex langata byd AY5179 | 2025-03-08 18:51 | 2024 | 2025-03-08 21:40 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 169 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 2.8167 | 0.010506 | 0.14708 | 31280 | 88105.3333
3154458 | Load management | 2025-03-09 19:10 | 2024 | 2025-03-10 10:41 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 931 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 15.5167 | 0.057876 | 0.81026 | 31280 | 485361.3333
3195714 | controlled | 2025-09-13 18:52 | 2025 | 2025-09-13 19:57 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 65 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2025 | 1.0833 | 0.0040407 | 0.05657 | 27872 | 30194.6667
3254337 | controlled | 2026-03-02 19:26 | 2025 | 2026-03-02 19:58 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 32 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.53333 | 0.0019893 | 0.02785 | 27872 | 14865.0667
3250982 | Controlled | 2026-02-26 08:14 | 2025 | 2026-02-26 08:25 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 11 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2026 | 0.18333 | 0.00068382 | 0.0095734 | 27872 | 5109.8667
2973373 | Load management due to unavailability of generation | 2022-12-14 18:57 | 2022 | 2022-12-14 20:40 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 103 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 1.7167 | 0.006403 | 0.089642 | 33290 | 57147.8333
2941314 | Soweto ex Langata on Load shedding | 2022-07-22 19:00 | 2022 | 2022-07-22 19:19 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 19 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 0.31667 | 0.0011811 | 0.016536 | 32658 | 10341.7
2946497 | Load management | 2022-08-16 19:48 | 2022 | 2022-08-16 22:13 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 145 | 3729.9 | 32658 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 2.4167 | 0.0090139 | 0.12619 | 32658 | 78923.5
2999114 | Load management | 2023-04-08 15:30 | 2022 | 2023-04-08 17:20 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 110 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 1.8333 | 0.0068382 | 0.095734 | 33290 | 61031.6667
3154069 | Load management | 2025-03-07 20:13 | 2024 | 2025-03-07 21:28 | Power Rationing | CONTROLLED INTERRUPTION | LOAD MANAGEMENT | Resolved | Nairobi | Nairobi West County | Non Programmed | 75 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.25 | 0.0046624 | 0.065273 | 31280 | 39100
3145383 | Load shedding due to generation shortfall | 2025-01-29 19:27 | 2024 | 2025-01-29 19:44 | Power Rationing | CONTROLLED INTERRUPTION | POWER RATIONING | Resolved | Nairobi | Nairobi West County | Non Programmed | 17 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.28333 | 0.0010568 | 0.014795 | 32702 | 9265.5667
3086716 | Sustained fault | 2024-05-01 09:56 | 2023 | 2024-05-01 15:20 | Underground cable | CABLE | FAULTY U/G MV CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 324 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 5.4 | 0.015469 | 0.21656 | 12107 | 65377.8
3179247 | Burnt cable termination to s/s 3692B | 2025-06-21 15:05 | 2024 | 2025-06-21 16:39 | Underground cable | CABLE | BURNT CABLE TERMINATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 94 | 2905.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 1.5667 | 0.0045521 | 0.063729 | 12217 | 19139.9667
3144805 | Sustained fault on Ngei ex Langata.Informed Wamalwa | 2025-01-27 20:02 | 2024 | 2025-01-27 22:05 | Underground cable | CABLE | FAULTY U/G MV CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 123 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 2.05 | 0.0058724 | 0.082214 | 12297 | 25208.85
3141926 | Sustained fault | 2025-01-15 22:02 | 2024 | 2025-01-15 22:07 | Underground cable | CABLE | FAULTY U/G MV CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 5 | 2864.6 | 12297 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 0.083333 | 0.00023872 | 0.003342 | 12297 | 1024.75
3081110 | Sustained fault on Ngei ex Langata byd AY 1195. Informed Mageto. | 2024-04-11 12:46 | 2023 | 2024-04-11 16:46 | Underground cable | CABLE | FAULTY U/G MV CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 240 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 4 | 0.011458 | 0.16042 | 12107 | 48428
3223590 | A trip on Soweto ex Langata not closing on SCADA awaiting operator | 2026-01-01 14:50 | 2025 | 2026-01-02 16:26 | Underground cable | CABLE | FAULTY U/G MV CABLE | Resolved | Nairobi | Nairobi West County | Non Programmed | 1536 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 25.6 | 0.095485 | 1.3368 | 27872 | 713523.2
3188865 | Soweto fault Tripped incomer 2 | 2025-08-11 14:37 | 2025 | 2025-08-12 20:45 | Underground cable | CABLE | BURNT CABLE TERMINATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 1808 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 30.1333 | 0.11239 | 1.5735 | 27872 | 839876.2667
3160400 | MAGADI EX LANGATA | 2025-03-30 03:03 | 2024 | 2025-03-30 19:41 | Surge diverter | EQUIPMENT FAILURE | FAULTY SURGE DIVERTER | Resolved | Nairobi | Nairobi West County | Non Programmed | 998 | 2812 | 5774 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 16.6333 | 0.046773 | 0.65482 | 5774 | 96040.8667
3103887 | off | 2024-07-17 15:10 | 2024 | 2024-07-17 16:14 | Circuit Breaker | EQUIPMENT FAILURE | FAULTY CIRCUIT BREAKER | Resolved | Nairobi | Nairobi West County | Non Programmed | 64 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 1.0667 | 0.0016067 | 0.022494 | 2832 | 3020.8
3081917 | Atrip on cb | 2024-04-14 19:06 | 2023 | 2024-04-14 19:49 | Circuit Breaker | EQUIPMENT FAILURE | FAULTY CIRCUIT BREAKER | Resolved | Nairobi | Nairobi West County | Non Programmed | 43 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.71667 | 0.002053 | 0.028741 | 12107 | 8676.6833
3028273 | Trip on fault | 2023-08-30 00:10 | 2023 | 2023-08-30 05:36 | Air Break Switch | EQUIPMENT FAILURE | ARCING AIR BREAK SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 326 | 2811.7 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 5.4333 | 0.015277 | 0.21388 | 5260 | 28579.3333
3167551 | sustained fault | 2025-04-26 20:48 | 2024 | 2025-04-27 12:53 | Air Break Switch | EQUIPMENT FAILURE | ARCING AIR BREAK SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 965 | 3729.9 | 31280 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 16.0833 | 0.059989 | 0.83985 | 31280 | 503086.6667
2956076 | Shattered pin insulator, conductor off pin insulator, vandalised stay wire | 2022-09-30 03:11 | 2022 | 2022-09-30 11:07 | Insulators | EQUIPMENT FAILURE | SHATTERED PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 476 | 2812 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 7.9333 | 0.022309 | 0.31232 | 5016 | 39793.6
2958759 | Repair faulty LBS 1118 | 2022-10-12 12:34 | 2022 | 2022-10-12 13:47 | Load Break Switch | EQUIPMENT FAILURE | FAULTY LBS SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 73 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 1.2167 | 0.0018327 | 0.025657 | 2561 | 3115.8833
3014386 | To repair faulty LBS 5306 | 2023-06-16 11:41 | 2022 | 2023-06-16 13:11 | Load Break Switch | EQUIPMENT FAILURE | FAULTY LBS SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 90 | 963.1 | 1938 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2023 | 1.5 | 0.0014447 | 0.020225 | 1938 | 2907
2998352 | Replace ARY5230 | 2023-04-06 11:02 | 2022 | 2023-04-06 12:51 | Load Break Switch | EQUIPMENT FAILURE | FAULTY LBS SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 109 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 1.8167 | 0.0051079 | 0.071511 | 5212 | 9468.4667
3083658 | Soweto ex Langata Beyond AY 5302 off awaiting operator, AY 5302 closing failure, | 2024-04-21 06:31 | 2023 | 2024-04-21 08:14 | Load Break Switch | EQUIPMENT FAILURE | FAULTY LBS SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 103 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.7167 | 0.006403 | 0.089642 | 33325 | 57207.9167
2986736 | Faulty VT at AY5179 | 2023-02-20 13:05 | 2022 | 2023-02-21 10:23 | Load Break Switch | EQUIPMENT FAILURE | FAULTY LBS SWITCH | Resolved | Nairobi | Nairobi West County | Non Programmed | 1278 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2023 | 21.3 | 0.079447 | 1.1123 | 33290 | 709077
3181126 | sustained fault | 2025-06-30 20:17 | 2024 | 2025-06-30 21:29 | Vandalism Related cases | VANDALISM | VANDALISED EQUIPMENT/ INSTALLATION | Resolved | Nairobi | Nairobi West County | Non Programmed | 72 | 963.1 | 2155 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 06-2025 | 1.2 | 0.0011557 | 0.01618 | 2155 | 2586
2990328 | Vandalized stay wire shorting the line | 2023-03-08 21:15 | 2022 | 2023-03-09 08:21 | Vandalised Stay Wire | VANDALISM | VANDALIZED STAY WIRE | Resolved | Nairobi | Nairobi West County | Non Programmed | 666 | 2812 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 11.1 | 0.031213 | 0.43698 | 5212 | 57853.2
3142997 | Incidence no: 3142997 has automatically been generated from shutdown no: 82406 | 2025-01-21 09:00 | 2024 | 2025-01-21 18:39 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 579 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 9.65 | 0.014536 | 0.2035 | 2958 | 28544.7
3150176 | Incidence no: 3150176 has automatically been generated from shutdown no: 82968 | 2025-02-20 09:07 | 2024 | 2025-02-20 22:26 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 799 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 13.3167 | 0.020059 | 0.28082 | 2964 | 39470.6
3155096 | Incidence no: 3155096 has automatically been generated from shutdown no: 83654 | 2025-03-11 09:00 | 2024 | 2025-03-11 17:58 | Planned Outage | CONTROLLED INTERRUPTION | PLANNED OUTAGE | Resolved | Nairobi | Nairobi West County | Programmed | 538 | 1506.3 | 2964 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 8.9667 | 0.013506 | 0.18909 | 2964 | 26577.2
3301066 | Sustained fault | 2026-04-01 14:11 | 2025 | 2026-04-01 17:01 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 170 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 2.8333 | 0.0057134 | 0.079988 | 3056 | 8658.6667
2971597 | To correct poor sag | 2022-12-06 15:07 | 2022 | 2022-12-06 16:10 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 63 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 1.05 | 0.0015816 | 0.022143 | 2561 | 2689.05
2998128 | Broken conductors | 2023-04-05 15:41 | 2022 | 2023-04-05 18:43 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 182 | 1506.3 | 2561 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2023 | 3.0333 | 0.0045691 | 0.063968 | 2561 | 7768.3667
3105591 | dIM LIGHTS | 2024-07-26 18:35 | 2024 | 2024-07-27 12:12 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 1057 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 17.6167 | 0.026536 | 0.3715 | 2832 | 49890.4
3093301 | Repair broken jumper | 2024-05-26 17:38 | 2023 | 2024-05-26 18:17 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 39 | 1506.3 | 2832 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 0.65 | 0.00097909 | 0.013707 | 2832 | 1840.8
3067469 | Sustained fault on Hardy ex Langata byd AY1104 Nyamweya informed | 2024-02-17 12:38 | 2023 | 2024-02-17 15:37 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 178 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 2.9667 | 0.0044687 | 0.062562 | 2807 | 8327.4333
3045235 | Hardy ex Langata sustained Byd AY1104 Nyamweya informed | 2023-11-09 13:59 | 2023 | 2023-11-09 17:22 | MV Conductor | CONDUCTORS | BROKEN HT TX DROPPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 203 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2023 | 3.3833 | 0.0050963 | 0.071348 | 2807 | 9497.0167
3024067 | Twisted conductors beyond CB, Knocked strut pole | 2023-08-07 11:15 | 2023 | 2023-08-07 16:55 | MV Conductor | CONDUCTORS | TWISTED MV CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 340 | 1506.3 | 2654 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 5.6667 | 0.0085357 | 0.1195 | 2654 | 15039.3333
3122557 | sustained fault | 2024-10-19 13:28 | 2024 | 2024-10-19 18:20 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 292 | 1506.3 | 2958 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2024 | 4.8667 | 0.0073307 | 0.10263 | 2958 | 14395.6
3081959 | Sustained fault on Kuwinda ex Langata byd ARY 5178. Informed Karen office | 2024-04-15 01:36 | 2023 | 2024-04-15 16:06 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 870 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 14.5 | 0.013965 | 0.19551 | 2020 | 29290
3082169 | Broken jumper before ARY5178 | 2024-04-15 17:27 | 2023 | 2024-04-15 18:51 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 84 | 963.1 | 2020 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.4 | 0.0013483 | 0.018877 | 2020 | 2828
2953573 | Sustained fault | 2022-09-18 18:48 | 2022 | 2022-09-18 21:13 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 145 | 963.1 | 1879 | 208002341 | KUWINDA EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 2.4167 | 0.0023275 | 0.032585 | 1879 | 4540.9167
3144282 | Sustained byd AY 122, Lion informed. | 2025-01-25 22:33 | 2024 | 2025-01-26 11:06 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 753 | 692.9 | 1188 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2025 | 12.55 | 0.0086959 | 0.12174 | 1188 | 14909.4
3166353 | controlled | 2025-04-22 13:26 | 2024 | 2025-04-22 13:36 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 10 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2025 | 0.16667 | 0.00011548 | 0.0016168 | 1206 | 201
3159602 | Broken jumper at cable take off | 2025-03-26 14:52 | 2024 | 2025-03-26 16:05 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 73 | 692.9 | 1206 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 1.2167 | 0.00084303 | 0.011802 | 1206 | 1467.3
2971887 | Karen Hospital ex Langata off awaiting operator | 2022-12-07 19:42 | 2022 | 2022-12-08 13:23 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 1061 | 692.9 | 1049 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 17.6833 | 0.012253 | 0.17154 | 1049 | 18549.8167
3227754 | Broken HT jumper | 2026-01-08 18:31 | 2025 | 2026-01-08 18:43 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 12 | 122.2 | 177 | 208001429 | OTIENDE EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2026 | 0.2 | 2.444e-05 | 0.00034216 | 177 | 35.4
2971383 | Langata | 2022-12-05 18:06 | 2022 | 2022-12-05 22:24 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 258 | 2811.7 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 4.3 | 0.01209 | 0.16926 | 5212 | 22411.6
3087694 | Sustained fault beyond AY5198 | 2024-05-04 03:10 | 2023 | 2024-05-04 11:50 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 520 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2024 | 8.6667 | 0.024368 | 0.34115 | 5690 | 49313.3333
3259000 | Controlled | 2026-03-08 18:00 | 2025 | 2026-03-09 18:16 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 15 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 0.25 | 0.00070292 | 0.0098409 | 6310 | 1577.5
3257957 | O/C | 2026-03-07 05:31 | 2025 | 2026-03-08 16:05 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 2074 | 2811.7 | 6310 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 34.5667 | 0.097191 | 1.3607 | 6310 | 218115.6667
3029768 | HT conductors shorting LV conductors | 2023-09-06 14:13 | 2023 | 2023-09-06 16:14 | MV Conductor | CONDUCTORS | CLASHING CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 121 | 2812 | 5260 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2023 | 2.0167 | 0.0056709 | 0.079392 | 5260 | 10607.6667
2954986 | MAGADI EX LANGATA | 2022-09-25 00:37 | 2022 | 2022-09-25 11:09 | MV Conductor | CONDUCTORS | CONDUCTOR OFF PIN INSULATOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 632 | 2812 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 10.5333 | 0.02962 | 0.41468 | 5016 | 52835.2
3149571 | sustained fault | 2025-02-17 16:53 | 2024 | 2025-02-17 19:24 | MV Conductor | CONDUCTORS | TWISTED MV CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 151 | 2811.7 | 5760 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 2.5167 | 0.0070761 | 0.099066 | 5760 | 14496
2956999 | Broken jumper beyond AY5198 | 2022-10-04 09:22 | 2022 | 2022-10-04 09:44 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 22 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 10-2022 | 0.36667 | 0.001031 | 0.014433 | 5016 | 1839.2
3351254 | Sustained fault Magadi ex Langata Broken jumper at cable take off George salat i | 2026-04-19 10:43 | 2025 | 2026-04-19 11:54 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 71 | 2811.7 | 6752 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2026 | 1.1833 | 0.0033272 | 0.04658 | 6752 | 7989.8667
3084426 | Sustained fault | 2024-04-23 14:45 | 2023 | 2024-04-23 17:22 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 157 | 2811.7 | 5690 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 2.6167 | 0.0073573 | 0.103 | 5690 | 14888.8333
2950378 | Sustained fault on Ngei ex Langata beyond AY195 | 2022-09-04 09:43 | 2022 | 2022-09-04 12:53 | MV Conductor | CONDUCTORS | BROKEN HT TX DROPPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 190 | 2865 | 11799 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 3.1667 | 0.0090725 | 0.12701 | 11799 | 37363.5
3157864 | Broken jumper | 2025-03-20 20:59 | 2024 | 2025-03-20 21:12 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 13 | 2864.6 | 12217 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2025 | 0.21667 | 0.00062066 | 0.0086893 | 12217 | 2647.0167
3083509 | Controlled to repair broken jumper at near source | 2024-04-20 10:55 | 2023 | 2024-04-20 19:08 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 493 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 8.2167 | 0.023537 | 0.32952 | 12107 | 99479.1833
3103917 | Off waiting operator | 2024-07-17 19:00 | 2024 | 2024-07-17 23:37 | MV Conductor | CONDUCTORS | BROKEN HT TX DROPPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 277 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2024 | 4.6167 | 0.0090251 | 0.12635 | 837 | 3864.15
3083320 | Sustained fault on Ndalat ex Langata. Informed Nyamweya | 2024-04-19 18:48 | 2023 | 2024-04-19 20:14 | MV Conductor | CONDUCTORS | BROKEN HT TX DROPPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 86 | 1954.9 | 837 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 1.4333 | 0.002802 | 0.039228 | 837 | 1199.7
3023781 | Sustained fault on Soweto ex Langata beyond AY5179. | 2023-08-05 19:10 | 2023 | 2023-08-06 11:15 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 965 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 16.0833 | 0.059989 | 0.83985 | 33295 | 535494.5833
3080956 | Soweto ex Langata sustained | 2024-04-11 05:10 | 2023 | 2024-04-11 12:08 | MV Conductor | CONDUCTORS | TWISTED MV CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 418 | 3729.9 | 33325 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 6.9667 | 0.025985 | 0.36379 | 33325 | 232164.1667
2991979 | Faulty spindle, twisted conductors, faulty 315kva TX - s/s 36374 | 2023-03-16 00:02 | 2022 | 2023-03-16 14:57 | MV Conductor | CONDUCTORS | TWISTED MV CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 895 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2023 | 14.9167 | 0.055638 | 0.77893 | 33290 | 496575.8333
3148991 | Burnt HT jumper at cable take off | 2025-02-14 10:58 | 2024 | 2025-02-14 11:34 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 36 | 3729.9 | 32702 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2025 | 0.6 | 0.0022379 | 0.031331 | 32702 | 19621.2
2973446 | Single phasing on Soweto ex Langata | 2022-12-15 06:30 | 2022 | 2022-12-15 13:20 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 410 | 3729.9 | 33290 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 12-2022 | 6.8333 | 0.025488 | 0.35683 | 33290 | 227481.6667
3062806 | Clashing conductors beyond AY5300 | 2024-01-27 15:28 | 2023 | 2024-01-27 16:57 | MV Conductor | CONDUCTORS | CLASHING CONDUCTORS | Resolved | Nairobi | Nairobi West County | Non Programmed | 89 | 3729.9 | 33331 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 01-2024 | 1.4833 | 0.0055327 | 0.077458 | 33331 | 49440.9833
3010113 | Feeder off on sustained fault | 2023-05-25 23:13 | 2022 | 2023-05-26 15:30 | MV Conductor | CONDUCTORS | BROKEN MV JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 977 | 3729.9 | 33284 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 05-2023 | 16.2833 | 0.060735 | 0.85029 | 33284 | 541974.4667
3024084 | Feeder off on sustained fault | 2023-08-07 19:35 | 2023 | 2023-08-08 13:24 | MV Conductor | CONDUCTORS | BROKEN MV CONDUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 1069 | 3729.9 | 33295 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2023 | 17.8167 | 0.066454 | 0.93036 | 33295 | 593205.9167
3264734 | Sustained fault on Hardy ex Langata, Siriba informed. | 2026-03-14 08:37 | 2025 | 2026-03-14 11:43 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 186 | 2016.5 | 3056 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 03-2026 | 3.1 | 0.0062511 | 0.087516 | 3056 | 9473.6
3068743 | Single phasing | 2024-02-22 12:45 | 2023 | 2024-02-22 16:45 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 240 | 1506.3 | 2807 | 208001428 | HARDY EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 02-2024 | 4 | 0.0060252 | 0.084353 | 2807 | 11228
3190217 | Sustained fault | 2025-08-18 11:00 | 2025 | 2025-08-18 16:26 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 326 | 0 | 0 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2025 | 5.4333 | 0 | 0 | 0 | 0
2936956 | Broken HT jumper at 122 | 2022-07-03 12:10 | 2022 | 2022-07-03 16:09 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 239 | 692.9 | 872 | 208001427 | KAREN HOSPITAL EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 3.9833 | 0.0027601 | 0.038641 | 872 | 3473.4667
2963240 | Broken conductor | 2022-11-02 05:39 | 2022 | 2022-11-02 09:39 | HT conductors | CONDUCTORS | BROKEN HT CODUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 240 | 2812 | 5212 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 11-2022 | 4 | 0.011248 | 0.15747 | 5212 | 20848
2956193 | Broken jumper at AY145 | 2022-09-30 13:48 | 2022 | 2022-09-30 16:24 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 156 | 2811.7 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2022 | 2.6 | 0.0073104 | 0.10235 | 5016 | 13041.6
2944164 | Broken jumper | 2022-08-04 20:25 | 2022 | 2022-08-05 12:30 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 965 | 2812 | 5016 | 208001430 | MAGADI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 08-2022 | 16.0833 | 0.045226 | 0.63317 | 5016 | 80674
3083477 | broken jumper at Y137 Julius attending | 2024-04-20 13:04 | 2023 | 2024-04-20 14:05 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 46 | 2864.6 | 12107 | 208002350 | NGEI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 04-2024 | 0.76667 | 0.0021962 | 0.030747 | 12107 | 9282.0333
2942234 | Broken HT conductors | 2022-07-27 09:08 | 2022 | 2022-07-27 16:04 | HT conductors | CONDUCTORS | BROKEN HT CODUCTOR | Resolved | Nairobi | Nairobi West County | Non Programmed | 416 | 1954.9 | 698 | 208002351 | NDALATI EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 07-2022 | 6.9333 | 0.013554 | 0.18976 | 698 | 4839.4667
3199231 | Controlled | 2025-09-29 15:46 | 2025 | 2025-09-29 16:10 | HT conductors | CONDUCTORS | BROKEN HT JUMPER | Resolved | Nairobi | Nairobi West County | Non Programmed | 24 | 3729.9 | 27872 | 208002349 | SOWETO EX LANGATA | LANGATA 66KV / 11KV ( 66 / 11 KV) | 2 | KAREN | 09-2025 | 0.4 | 0.001492 | 0.020887 | 27872 | 11148.8